## Info
Name | RCX
Version | 2.1-1-01
Description | MODEL 2.1-1-01

## en
RCX-2.1-1-01 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Overview
System
|  |  | Controller | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbus address | Active Modbus unit ID (ModbusUnitID)
|  |  | BACnet MSTP address | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet device ID | BACnet device ID (BACnetDeviceID)
|  |  | Sum alarm | Sum Alarm (RC_SumAlarm)
Room
|  |  | Controller state | Current state (RC_ControllerState)
|  |  | Mode | Current controller mode (RC_ControllerMode)
|  |  | Room temperature [°C] | Room temperature (RC_RoomTemp)
|  |  | Supply air temperature [°C] | Supply air temperature (RC_SupplyAirTemp)
|  |  | Room setpoint [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Setpoint adjustment [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC fan speed [%] | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2 level [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Room humidity [%] | Relative humidity (RC_Humidity)
|  |  | VOC index | VOC index (RC_VOC)
|  |  | Presence detection | Presence indication (RC_Presence)
|  |  | Condensation | Condensation indication (RC_DICondensation)
Extra zone
|  |  | Extra zone temperature [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Extra zone setpoint [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Extra zone active output | Extra Zone active (RC_ExtraZoneActive)
Actual values
Room Control Sequence
|  |  | Sequence 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sequence 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sequence 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Actual values
|  |  | Mode | Current controller mode (RC_ControllerMode)
|  |  | Room temperature [°C] | Room temperature (RC_RoomTemp)
|  |  | Room setpoint [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Setpoint adjustment [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Heating demand [%] | Room PID heat output (RC_PIDHeatDemand)
|  |  | Cooling demand [%] | Room PID cool output (RC_PIDCoolDemand)
|  |  | Heating output [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Heating 2 output [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Cooling output [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Cooling 2 output [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | VAV output [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | VAV 2 output [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-over temperature | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-over state | Change-over status (RC_ChangeOverState)
|  |  | Change-over output [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-over VAV temperature | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-over VAV state | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Change-over VAV output [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | 6-way valve output [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2 level [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2 setpoint [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Relay output
|  |  | Relay state | Value set for output (IoDo_3_value)
Inputs/Outputs
Universal inputs
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universal outputs
|  |  | UO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analog outputs
|  |  | AO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Internal sensors
|  |  | Room temperature [°C] | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2 sensor [ppm] | Filtered value from sensor (IoAnaIn_8_value)
|  |  | RH sensor [%] | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC sensor | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR sensor | Filtered value from sensor (IoDiIn_4_value)
Alarms
Alarms
|  |  | Sum alarm | Sum Alarm (RC_SumAlarm)
|  |  | Sensor error | Sensor error alarm (RC_AlarmSensorError)
|  |  | High room temperature | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Low room temperature | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | High CO2 level | High CO2 alarm (RC_AlarmCO2High)
|  |  | External alarm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Output in manual mode | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Temperature sensor error code | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Humidity sensor error code | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | VOC sensor error code | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | CO2 sensor error code | Detailed fault description (IoAnaIn_8_errorFlags)
About
Device ID
|  |  | Serial number | (SerialNumberString)
|  |  | Name | (ControllerName)
|  |  | Description | Controller description (ControllerDescription)
|  |  | Location | Controller location (ControllerLocation)
|  |  | Project | (ControllerProject)
Custom menus
Custom menu 1
|  |  | Title | Title for Custom Menu 1 (CM1Title)
|  |  | Current value | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Current alternative | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Current alternative | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Current alternative | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Current alternative | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Current alternative | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Current alternative | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Current alternative | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Current alternative | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Current alternative | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Current alternative | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Current alternative | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Current alternative | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Current alternative | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Current alternative | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Current alternative | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Current alternative | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Current alternative | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Current alternative | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Current alternative | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Current alternative | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Current alternative | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Current alternative index | Current alternative for Custom Menu 1 (CM1CurrentAlt)
Custom menu 2
|  |  | Title | Title for Custom Menu 2 (CM2Title)
|  |  | Current value | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Current alternative | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Current alternative | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Current alternative | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Current alternative | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Current alternative | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Current alternative | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Current alternative | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Current alternative | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Current alternative | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Current alternative | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Current alternative | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Current alternative | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Current alternative | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Current alternative | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Current alternative | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Current alternative | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Current alternative | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Current alternative | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Current alternative | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Current alternative | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Current alternative | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Current alternative index | Current alternative for Custom Menu 2 (CM2CurrentAlt)
Custom menu 3
|  |  | Title | Title for Custom Menu 3 (CM3Title)
|  |  | Current value | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Current alternative | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Current alternative | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Current alternative | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Current alternative | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Current alternative | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Current alternative | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Current alternative | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Current alternative | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Current alternative | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Current alternative | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Current alternative | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Current alternative | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Current alternative | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Current alternative | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Current alternative | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Current alternative | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Current alternative | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Current alternative | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Current alternative | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Current alternative | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Current alternative | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Current alternative index | Current alternative for Custom Menu 3 (CM3CurrentAlt)
Custom menu 4
|  |  | Title | Title for Custom Menu 4 (CM4Title)
|  |  | Current value | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Current alternative | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Current alternative | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Current alternative | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Current alternative | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Current alternative | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Current alternative | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Current alternative | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Current alternative | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Current alternative | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Current alternative | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Current alternative | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Current alternative | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Current alternative | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Current alternative | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Current alternative | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Current alternative | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Current alternative | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Current alternative | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Current alternative | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Current alternative | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Current alternative | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Current alternative index | Current alternative for Custom Menu 4 (CM4CurrentAlt)
Custom menu 5
|  |  | Title | Title for Custom Menu 5 (CM5Title)
|  |  | Current value | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Current alternative | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Current alternative | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Current alternative | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Current alternative | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Current alternative | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Current alternative | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Current alternative | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Current alternative | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Current alternative | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Current alternative | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Current alternative | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Current alternative | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Current alternative | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Current alternative | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Current alternative | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Current alternative | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Current alternative | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Current alternative | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Current alternative | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Current alternative | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Current alternative | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Current alternative index | Current alternative for Custom Menu 5 (CM5CurrentAlt)
Custom menu 6
|  |  | Title | Title for Custom Menu 6 (CM6Title)
|  |  | Current value | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Current alternative | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Current alternative | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Current alternative | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Current alternative | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Current alternative | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Current alternative | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Current alternative | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Current alternative | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Current alternative | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Current alternative | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Current alternative | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Current alternative | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Current alternative | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Current alternative | Text for alternative 14 for Custom Menu 6 (CM6Alt14Text)
|  |  | Current alternative | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Current alternative | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Current alternative | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Current alternative | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Current alternative | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Current alternative | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Current alternative | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Current alternative index | Current alternative for Custom Menu 6 (CM6CurrentAlt)
Custom menu 7
|  |  | Title | Title for Custom Menu 7 (CM7Title)
|  |  | Current value | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Current alternative | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Current alternative | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Current alternative | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Current alternative | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Current alternative | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Current alternative | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Current alternative | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Current alternative | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Current alternative | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Current alternative | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Current alternative | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Current alternative | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Current alternative | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Current alternative | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Current alternative | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Current alternative | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Current alternative | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Current alternative | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Current alternative | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Current alternative | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Current alternative | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Current alternative index | Current alternative for Custom Menu 7 (CM7CurrentAlt)
Custom menu 8
|  |  | Title | Title for Custom Menu 8 (CM8Title)
|  |  | Current value | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Current alternative | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Current alternative | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Current alternative | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Current alternative | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Current alternative | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Current alternative | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Current alternative | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Current alternative | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Current alternative | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Current alternative | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Current alternative | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Current alternative | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Current alternative | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Current alternative | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Current alternative | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Current alternative | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Current alternative | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Current alternative | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Current alternative | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Current alternative | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Current alternative | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Current alternative index | Current alternative for Custom Menu 8 (CM8CurrentAlt)
Configuration
Control functions
Room Control Sequence
|  |  | Sequence 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sequence 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sequence 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Heat
|  |  | Max limit [%] | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min limit [%] | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Fan off delay for electric heater | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Follow change-over state | Heat1 included in change-over function (RC_Heat1InChangeOver)
Heat 2
|  |  | Max limit [%] | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min limit [%] | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Fan off delay for electric heater | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Follow change-over state | Heat2 included in change-over function (RC_Heat2InChangeOver)
Cool
|  |  | Max limit [%] | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min limit [%] | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Set to max at forced ventilation state | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Turn off output when fan is off | Turn off Cool1 output when the fan is off (RC_Cool1OffWhenFanIsOff)
|  |  | Follow change-over state | Cool1 included in change-over function (RC_Cool1InChangeOver)
Cool 2
|  |  | Max limit [%] | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min limit [%] | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Set to max at forced ventilation state | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Turn off output when fan is off | Turn off Cool2 output when the fan is off (RC_Cool2OffWhenFanIsOff)
|  |  | Follow change-over state | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Max limit [%] | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min limit, off [%] | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min limit, unoccupied [%] | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min limit, standby [%] | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min limit, occupied [%] | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min limit, forced ventilation [%] | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Set to max at forced ventilation state | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Max limit when heating [%] | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Follow change-over state | VAV1 included in change-over function (RC_VAV1InChangeOver)
|  |  | Start VAV when previous cool sequence reaches [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Start VAV when previous heat sequence reaches [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VAV 2
|  |  | Max limit [%] | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min limit, off [%] | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min limit, unoccupied [%] | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min limit, standby [%] | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min limit, occupied [%] | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min limit, forced ventilation [%] | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Set to max at forced ventilation state | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Max limit when heating [%] | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Follow change-over state | VAV2 included in change-over function (RC_VAV2InChangeOver)
|  |  | Start VAV when previous cool sequence reaches [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Start VAV when previous heat sequence reaches [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VAV control source
|  |  | Cooling demand | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2 level | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC index | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Humidity | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Max limit [%] | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min limit [%] | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Mode | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-over temperature [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Heating hysteresis [°C] | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Cooling hysteresis [°C] | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Valve delay time [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over VAV
|  |  | Max limit [%] | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min limit, off [%] | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min limit, unoccupied [%] | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min limit, standby [%] | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min limit, occupied [%] | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min limit, forced ventilation [%] | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Set to max at forced ventilation state | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Mode | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-over temperature [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Heating hysteresis [°C] | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Cooling hysteresis [°C] | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Valve delay time [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
|  |  | Start VAV when previous cool sequence reaches [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Start VAV when previous heat sequence reaches [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
6-way valve
|  |  | Seq 1 fully open [V] | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Seq 1 start opening [V] | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Seq 2 fully open [V] | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Seq 2 start opening [V] | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Center point [V] | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Center point hysteresis [%] | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Sequence order | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Follow change-over state | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Controller state
|  |  | Preset state | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Shutdown state | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Window open state | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Time in forced ventilation state [min] | Bypass time (minutes) (RC_BypassTime)
Forced ventilation
|  |  | Active when | Forced ventilation function (RC_ForcedVentMode)
|  |  | Start limit [%] | Forced ventilation start limit (RC_ForcedVentStartLimit)
Presence detection
|  |  | Presence state | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Active delay [min] | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Inactive delay [min] | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2 activation | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2 level [ppm] | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2 hysteresis [ppm] | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Use internal PIR for presence | Use internal PIR sensor for presence detection (RC_PIRPresence)
Extra zone
Extra zone
|  |  | Extra zone function | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Disabled below state | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Disable if main zone mode differs from function | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min limit [%] | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Max limit [%] | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Inputs/Outputs
Universal inputs
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universal outputs
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | UO1 period thermal valve [s] | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | UO1 control signal | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | UO2 period thermal valve [s] | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | UO2 control signal | Unit converter (IoAnaOut_2_unit)
Analog outputs
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO1 control signal | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | AO2 control signal | Unit converter (IoAnaOut_4_unit)
Fan control
Fan control source
|  |  | Room controller | Select fan control mode (RC_FanControlMode)
|  |  | CO2 level | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Humidity | Fan is controlled by humidity output (RC_FanControlHumidity)
EC Fan control
|  |  | Speed at no demand | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Off below demand [%] | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysteresis for fan speed decrease [%] | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Start speed [%] | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Max speed in auto mode [%] | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Forced ventilation speed | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Forced ventilation speed [%] | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Speed 1 output [%] | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Speed 2 output [%] | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Speed 3 output [%] | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Mould protection | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Fan kick start
|  |  | Kick-start time [s] | Fan kick start time (RC_FanKickStartTime)
Fan off delay
|  |  | Off delay time [s] | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Minimum speed | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Fan boost
|  |  | Mode | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Boost time [s] | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-band | Fan boost P band (RC_FanBoostPBand)
Display and menus
Display
|  |  | Start screen | What to display during device startup (DisplayStartupMode)
|  |  | View mode | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Setpoint mode | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | Round CO2 value to nearest | Min step for CO2 value (RC_CO2Step)
|  |  | Brightness full [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Dim timeout, 0 = Always full [s] | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Brightness dimmed [%] | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Off timeout, 0 = Never off [s] | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Idle display
|  |  | Temperature/setpoint | Show temperature/setpoint in idle view (App_IdleViewTemperature)
|  |  | CO2 level | Show CO2 value in idle view (App_IdleViewCO2)
|  |  | Room humidity | Show humidity in idle view (App_IdleViewHumidity)
|  |  | VOC index | Show VOC in idle view (App_IdleViewVOC)
|  |  | Controller state | Show mode in idle view (App_IdleViewMode)
Menu
|  |  | Setpoint adjust page | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Mode menu page | Enable Mode menu page (App_EnableMenuMode)
|  |  | Change-over menu page | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Fan menu page | Enable Fan menu page (App_EnableMenuFan)
|  |  | Forced ventilation menu page | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Forced ventilation extended run | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Temperature/setpoint page | Enable Temperature menu page (App_EnableMenuTemp)
|  |  | Humidity menu page | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | CO2 menu page | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | VOC menu page | Enable VOC menu page (App_EnableMenuVOC)
Display order
|  |  | Display position 1 | Display position 1 (DisplayPosition1)
|  |  | Display position 2 | Display position 2 (DisplayPosition2)
|  |  | Display position 3 | Display position 3 (DisplayPosition3)
|  |  | Display position 4 | Display position 4 (DisplayPosition4)
|  |  | Display position 5 | Display position 5 (DisplayPosition5)
|  |  | Display position 6 | Display position 6 (DisplayPosition6)
|  |  | Display position 7 | Display position 7 (DisplayPosition7)
|  |  | Display position 8 | Display position 8 (DisplayPosition8)
|  |  | Display position 9 | Display position 9 (DisplayPosition9)
|  |  | Display position 10 | Display position 10 (DisplayPosition10)
|  |  | Display position 11 | Display position 11 (DisplayPosition11)
|  |  | Display position 12 | Display position 12 (DisplayPosition12)
Custom menu options
|  |  | Custom menu 1 | Enable Custom Menu 1 (CM1Enabled)
|  |  | Custom menu 2 | Enable Custom Menu 2 (CM2Enabled)
|  |  | Custom menu 3 | Enable Custom Menu 3 (CM3Enabled)
|  |  | Custom menu 4 | Enable Custom Menu 4 (CM4Enabled)
|  |  | Custom menu 5 | Enable Custom Menu 5 (CM5Enabled)
|  |  | Custom menu 6 | Enable Custom Menu 6 (CM6Enabled)
|  |  | Custom menu 7 | Enable Custom Menu 7 (CM7Enabled)
|  |  | Custom menu 8 | Enable Custom Menu 8 (CM8Enabled)
Mode menu options
|  |  | Menu title text | Mode menu title (App_ModeMenuTitle)
|  |  | Mode Off enable | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Mode Unoccupied enable | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Mode Standby enable | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Mode Occupied enable | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Mode Forced ventilation enable | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Mode Off text | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Mode Unoccupied text | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Mode Standby text | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Mode Occupied text | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Mode Forced ventilation text | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Mode Auto text | Mode menu Auto state text (App_ModeMenuAutoText)
Change-over menu options
|  |  | Menu title text | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | State Heat enable | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | State Cool enable | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | State Auto enable | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | State Heat text | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | State Cool text | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | State Auto text | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
Led indication
|  |  | Brightness [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 led indication | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Yellow led CO2 level [ppm] | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Red led CO2 level [ppm] | CO2 level for red led (RC_CO2LevelRed)
Custom Texts
|  |  | View mode | When to show the custom text (rt_text_visability)
|  |  | Display mode | Single or dual row text in display (rt_text_mode)
|  |  | Scroll mode | Scroll mode (rt_text_display_scroll_mode)
|  |  | Font | What font to use for the display text (rt_text_font)
|  |  | Scroll delay [ms] | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Custom text timer value [s] | Time to show the custom text (rt_text_timeleft)
|  |  | Custom text row 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Custom text row 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Custom text 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Custom text 2 | String to show on row 2 in the display (rt_text_row_2)
Custom menus
Custom menu 1
|  |  | Title | Title for Custom Menu 1 (CM1Title)
|  |  | Current value | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Alternative 1 - Text | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Alternative 1 - Value | Value for alternative 1 for Custom Menu 1 (CM1Alt1Value)
|  |  | Alternative 2 - Text | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Alternative 2 - Value | Value for alternative 2 for Custom Menu 1 (CM1Alt2Value)
|  |  | Alternative 3 - Text | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Alternative 3 - Value | Value for alternative 3 for Custom Menu 1 (CM1Alt3Value)
|  |  | Alternative 4 - Text | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Alternative 4 - Value | Value for alternative 4 for Custom Menu 1 (CM1Alt4Value)
|  |  | Alternative 5 - Text | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Alternative 5 - Value | Value for alternative 5 for Custom Menu 1 (CM1Alt5Value)
|  |  | Alternative 6 - Text | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Alternative 6 - Value | Value for alternative 6 for Custom Menu 1 (CM1Alt6Value)
|  |  | Alternative 7 - Text | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Alternative 7 - Value | Value for alternative 7 for Custom Menu 1 (CM1Alt7Value)
|  |  | Alternative 8 - Text | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Alternative 8 - Value | Value for alternative 8 for Custom Menu 1 (CM1Alt8Value)
|  |  | Alternative 9 - Text | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Alternative 9 - Value | Value for alternative 9 for Custom Menu 1 (CM1Alt9Value)
|  |  | Alternative 10 - Text | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Alternative 10 - Value | Value for alternative 10 for Custom Menu 1 (CM1Alt10Value)
|  |  | Alternative 11 - Text | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Alternative 11 - Value | Value for alternative 11 for Custom Menu 1 (CM1Alt11Value)
|  |  | Alternative 12 - Text | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Alternative 12 - Value | Value for alternative 12 for Custom Menu 1 (CM1Alt12Value)
|  |  | Alternative 13 - Text | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Alternative 13 - Value | Value for alternative 13 for Custom Menu 1 (CM1Alt13Value)
|  |  | Alternative 14 - Text | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Alternative 14 - Value | Value for alternative 14 for Custom Menu 1 (CM1Alt14Value)
|  |  | Alternative 15 - Text | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Alternative 15 - Value | Value for alternative 15 for Custom Menu 1 (CM1Alt15Value)
|  |  | Alternative 16 - Text | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Alternative 16 - Value | Value for alternative 16 for Custom Menu 1 (CM1Alt16Value)
|  |  | Alternative 17 - Text | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Alternative 17 - Value | Value for alternative 17 for Custom Menu 1 (CM1Alt17Value)
|  |  | Alternative 18 - Text | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Alternative 18 - Value | Value for alternative 18 for Custom Menu 1 (CM1Alt18Value)
|  |  | Alternative 19 - Text | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Alternative 19 - Value | Value for alternative 19 for Custom Menu 1 (CM1Alt19Value)
|  |  | Alternative 20 - Text | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Alternative 20 - Value | Value for alternative 20 for Custom Menu 1 (CM1Alt20Value)
|  |  | Alternative 21 - Text | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Alternative 21 - Value | Value for alternative 21 for Custom Menu 1 (CM1Alt21Value)
Custom menu 2
|  |  | Title | Title for Custom Menu 2 (CM2Title)
|  |  | Current value | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Alternative 1 - Text | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Alternative 1 - Value | Value for alternative 1 for Custom Menu 2 (CM2Alt1Value)
|  |  | Alternative 2 - Text | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Alternative 2 - Value | Value for alternative 2 for Custom Menu 2 (CM2Alt2Value)
|  |  | Alternative 3 - Text | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Alternative 3 - Value | Value for alternative 3 for Custom Menu 2 (CM2Alt3Value)
|  |  | Alternative 4 - Text | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Alternative 4 - Value | Value for alternative 4 for Custom Menu 2 (CM2Alt4Value)
|  |  | Alternative 5 - Text | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Alternative 5 - Value | Value for alternative 5 for Custom Menu 2 (CM2Alt5Value)
|  |  | Alternative 6 - Text | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Alternative 6 - Value | Value for alternative 6 for Custom Menu 2 (CM2Alt6Value)
|  |  | Alternative 7 - Text | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Alternative 7 - Value | Value for alternative 7 for Custom Menu 2 (CM2Alt7Value)
|  |  | Alternative 8 - Text | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Alternative 8 - Value | Value for alternative 8 for Custom Menu 2 (CM2Alt8Value)
|  |  | Alternative 9 - Text | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Alternative 9 - Value | Value for alternative 9 for Custom Menu 2 (CM2Alt9Value)
|  |  | Alternative 10 - Text | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Alternative 10 - Value | Value for alternative 10 for Custom Menu 2 (CM2Alt10Value)
|  |  | Alternative 11 - Text | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Alternative 11 - Value | Value for alternative 11 for Custom Menu 2 (CM2Alt11Value)
|  |  | Alternative 12 - Text | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Alternative 12 - Value | Value for alternative 12 for Custom Menu 2 (CM2Alt12Value)
|  |  | Alternative 13 - Text | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Alternative 13 - Value | Value for alternative 13 for Custom Menu 2 (CM2Alt13Value)
|  |  | Alternative 14 - Text | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Alternative 14 - Value | Value for alternative 14 for Custom Menu 2 (CM2Alt14Value)
|  |  | Alternative 15 - Text | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Alternative 15 - Value | Value for alternative 15 for Custom Menu 2 (CM2Alt15Value)
|  |  | Alternative 16 - Text | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Alternative 16 - Value | Value for alternative 16 for Custom Menu 2 (CM2Alt16Value)
|  |  | Alternative 17 - Text | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Alternative 17 - Value | Value for alternative 17 for Custom Menu 2 (CM2Alt17Value)
|  |  | Alternative 18 - Text | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Alternative 18 - Value | Value for alternative 18 for Custom Menu 2 (CM2Alt18Value)
|  |  | Alternative 19 - Text | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Alternative 19 - Value | Value for alternative 19 for Custom Menu 2 (CM2Alt19Value)
|  |  | Alternative 20 - Text | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Alternative 20 - Value | Value for alternative 20 for Custom Menu 2 (CM2Alt20Value)
|  |  | Alternative 21 - Text | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Alternative 21 - Value | Value for alternative 21 for Custom Menu 2 (CM2Alt21Value)
Custom menu 3
|  |  | Title | Title for Custom Menu 3 (CM3Title)
|  |  | Current value | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Alternative 1 - Text | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Alternative 1 - Value | Value for alternative 1 for Custom Menu 3 (CM3Alt1Value)
|  |  | Alternative 2 - Text | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Alternative 2 - Value | Value for alternative 2 for Custom Menu 3 (CM3Alt2Value)
|  |  | Alternative 3 - Text | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Alternative 3 - Value | Value for alternative 3 for Custom Menu 3 (CM3Alt3Value)
|  |  | Alternative 4 - Text | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Alternative 4 - Value | Value for alternative 4 for Custom Menu 3 (CM3Alt4Value)
|  |  | Alternative 5 - Text | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Alternative 5 - Value | Value for alternative 5 for Custom Menu 3 (CM3Alt5Value)
|  |  | Alternative 6 - Text | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Alternative 6 - Value | Value for alternative 6 for Custom Menu 3 (CM3Alt6Value)
|  |  | Alternative 7 - Text | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Alternative 7 - Value | Value for alternative 7 for Custom Menu 3 (CM3Alt7Value)
|  |  | Alternative 8 - Text | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Alternative 8 - Value | Value for alternative 8 for Custom Menu 3 (CM3Alt8Value)
|  |  | Alternative 9 - Text | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Alternative 9 - Value | Value for alternative 9 for Custom Menu 3 (CM3Alt9Value)
|  |  | Alternative 10 - Text | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Alternative 10 - Value | Value for alternative 10 for Custom Menu 3 (CM3Alt10Value)
|  |  | Alternative 11 - Text | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Alternative 11 - Value | Value for alternative 11 for Custom Menu 3 (CM3Alt11Value)
|  |  | Alternative 12 - Text | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Alternative 12 - Value | Value for alternative 12 for Custom Menu 3 (CM3Alt12Value)
|  |  | Alternative 13 - Text | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Alternative 13 - Value | Value for alternative 13 for Custom Menu 3 (CM3Alt13Value)
|  |  | Alternative 14 - Text | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Alternative 14 - Value | Value for alternative 14 for Custom Menu 3 (CM3Alt14Value)
|  |  | Alternative 15 - Text | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Alternative 15 - Value | Value for alternative 15 for Custom Menu 3 (CM3Alt15Value)
|  |  | Alternative 16 - Text | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Alternative 16 - Value | Value for alternative 16 for Custom Menu 3 (CM3Alt16Value)
|  |  | Alternative 17 - Text | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Alternative 17 - Value | Value for alternative 17 for Custom Menu 3 (CM3Alt17Value)
|  |  | Alternative 18 - Text | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Alternative 18 - Value | Value for alternative 18 for Custom Menu 3 (CM3Alt18Value)
|  |  | Alternative 19 - Text | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Alternative 19 - Value | Value for alternative 19 for Custom Menu 3 (CM3Alt19Value)
|  |  | Alternative 20 - Text | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Alternative 20 - Value | Value for alternative 20 for Custom Menu 3 (CM3Alt20Value)
|  |  | Alternative 21 - Text | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Alternative 21 - Value | Value for alternative 21 for Custom Menu 3 (CM3Alt21Value)
Custom menu 4
|  |  | Title | Title for Custom Menu 4 (CM4Title)
|  |  | Current value | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Alternative 1 - Text | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Alternative 1 - Value | Value for alternative 1 for Custom Menu 4 (CM4Alt1Value)
|  |  | Alternative 2 - Text | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Alternative 2 - Value | Value for alternative 2 for Custom Menu 4 (CM4Alt2Value)
|  |  | Alternative 3 - Text | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Alternative 3 - Value | Value for alternative 3 for Custom Menu 4 (CM4Alt3Value)
|  |  | Alternative 4 - Text | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Alternative 4 - Value | Value for alternative 4 for Custom Menu 4 (CM4Alt4Value)
|  |  | Alternative 5 - Text | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Alternative 5 - Value | Value for alternative 5 for Custom Menu 4 (CM4Alt5Value)
|  |  | Alternative 6 - Text | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Alternative 6 - Value | Value for alternative 6 for Custom Menu 4 (CM4Alt6Value)
|  |  | Alternative 7 - Text | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Alternative 7 - Value | Value for alternative 7 for Custom Menu 4 (CM4Alt7Value)
|  |  | Alternative 8 - Text | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Alternative 8 - Value | Value for alternative 8 for Custom Menu 4 (CM4Alt8Value)
|  |  | Alternative 9 - Text | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Alternative 9 - Value | Value for alternative 9 for Custom Menu 4 (CM4Alt9Value)
|  |  | Alternative 10 - Text | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Alternative 10 - Value | Value for alternative 10 for Custom Menu 4 (CM4Alt10Value)
|  |  | Alternative 11 - Text | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Alternative 11 - Value | Value for alternative 11 for Custom Menu 4 (CM4Alt11Value)
|  |  | Alternative 12 - Text | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Alternative 12 - Value | Value for alternative 12 for Custom Menu 4 (CM4Alt12Value)
|  |  | Alternative 13 - Text | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Alternative 13 - Value | Value for alternative 13 for Custom Menu 4 (CM4Alt13Value)
|  |  | Alternative 14 - Text | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Alternative 14 - Value | Value for alternative 14 for Custom Menu 4 (CM4Alt14Value)
|  |  | Alternative 15 - Text | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Alternative 15 - Value | Value for alternative 15 for Custom Menu 4 (CM4Alt15Value)
|  |  | Alternative 16 - Text | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Alternative 16 - Value | Value for alternative 16 for Custom Menu 4 (CM4Alt16Value)
|  |  | Alternative 17 - Text | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Alternative 17 - Value | Value for alternative 17 for Custom Menu 4 (CM4Alt17Value)
|  |  | Alternative 18 - Text | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Alternative 18 - Value | Value for alternative 18 for Custom Menu 4 (CM4Alt18Value)
|  |  | Alternative 19 - Text | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Alternative 19 - Value | Value for alternative 19 for Custom Menu 4 (CM4Alt19Value)
|  |  | Alternative 20 - Text | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Alternative 20 - Value | Value for alternative 20 for Custom Menu 4 (CM4Alt20Value)
|  |  | Alternative 21 - Text | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Alternative 21 - Value | Value for alternative 21 for Custom Menu 4 (CM4Alt21Value)
Custom menu 5
|  |  | Title | Title for Custom Menu 5 (CM5Title)
|  |  | Current value | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Alternative 1 - Text | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Alternative 1 - Value | Value for alternative 1 for Custom Menu 5 (CM5Alt1Value)
|  |  | Alternative 2 - Text | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Alternative 2 - Value | Value for alternative 2 for Custom Menu 5 (CM5Alt2Value)
|  |  | Alternative 3 - Text | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Alternative 3 - Value | Value for alternative 3 for Custom Menu 5 (CM5Alt3Value)
|  |  | Alternative 4 - Text | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Alternative 4 - Value | Value for alternative 4 for Custom Menu 5 (CM5Alt4Value)
|  |  | Alternative 5 - Text | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Alternative 5 - Value | Value for alternative 5 for Custom Menu 5 (CM5Alt5Value)
|  |  | Alternative 6 - Text | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Alternative 6 - Value | Value for alternative 6 for Custom Menu 5 (CM5Alt6Value)
|  |  | Alternative 7 - Text | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Alternative 7 - Value | Value for alternative 7 for Custom Menu 5 (CM5Alt7Value)
|  |  | Alternative 8 - Text | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Alternative 8 - Value | Value for alternative 8 for Custom Menu 5 (CM5Alt8Value)
|  |  | Alternative 9 - Text | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Alternative 9 - Value | Value for alternative 9 for Custom Menu 5 (CM5Alt9Value)
|  |  | Alternative 10 - Text | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Alternative 10 - Value | Value for alternative 10 for Custom Menu 5 (CM5Alt10Value)
|  |  | Alternative 11 - Text | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Alternative 11 - Value | Value for alternative 11 for Custom Menu 5 (CM5Alt11Value)
|  |  | Alternative 12 - Text | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Alternative 12 - Value | Value for alternative 12 for Custom Menu 5 (CM5Alt12Value)
|  |  | Alternative 13 - Text | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Alternative 13 - Value | Value for alternative 13 for Custom Menu 5 (CM5Alt13Value)
|  |  | Alternative 14 - Text | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Alternative 14 - Value | Value for alternative 14 for Custom Menu 5 (CM5Alt14Value)
|  |  | Alternative 15 - Text | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Alternative 15 - Value | Value for alternative 15 for Custom Menu 5 (CM5Alt15Value)
|  |  | Alternative 16 - Text | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Alternative 16 - Value | Value for alternative 16 for Custom Menu 5 (CM5Alt16Value)
|  |  | Alternative 17 - Text | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Alternative 17 - Value | Value for alternative 17 for Custom Menu 5 (CM5Alt17Value)
|  |  | Alternative 18 - Text | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Alternative 18 - Value | Value for alternative 18 for Custom Menu 5 (CM5Alt18Value)
|  |  | Alternative 19 - Text | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Alternative 19 - Value | Value for alternative 19 for Custom Menu 5 (CM5Alt19Value)
|  |  | Alternative 20 - Text | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Alternative 20 - Value | Value for alternative 20 for Custom Menu 5 (CM5Alt20Value)
|  |  | Alternative 21 - Text | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Alternative 21 - Value | Value for alternative 21 for Custom Menu 5 (CM5Alt21Value)
Custom menu 6
|  |  | Title | Title for Custom Menu 6 (CM6Title)
|  |  | Current value | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Alternative 1 - Text | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Alternative 1 - Value | Value for alternative 1 for Custom Menu 6 (CM6Alt1Value)
|  |  | Alternative 2 - Text | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Alternative 2 - Value | Value for alternative 2 for Custom Menu 6 (CM6Alt2Value)
|  |  | Alternative 3 - Text | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Alternative 3 - Value | Value for alternative 3 for Custom Menu 6 (CM6Alt3Value)
|  |  | Alternative 4 - Text | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Alternative 4 - Value | Value for alternative 4 for Custom Menu 6 (CM6Alt4Value)
|  |  | Alternative 5 - Text | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Alternative 5 - Value | Value for alternative 5 for Custom Menu 6 (CM6Alt5Value)
|  |  | Alternative 6 - Text | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Alternative 6 - Value | Value for alternative 6 for Custom Menu 6 (CM6Alt6Value)
|  |  | Alternative 7 - Text | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Alternative 7 - Value | Value for alternative 7 for Custom Menu 6 (CM6Alt7Value)
|  |  | Alternative 8 - Text | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Alternative 8 - Value | Value for alternative 8 for Custom Menu 6 (CM6Alt8Value)
|  |  | Alternative 9 - Text | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Alternative 9 - Value | Value for alternative 9 for Custom Menu 6 (CM6Alt9Value)
|  |  | Alternative 10 - Text | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Alternative 10 - Value | Value for alternative 10 for Custom Menu 6 (CM6Alt10Value)
|  |  | Alternative 11 - Text | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Alternative 11 - Value | Value for alternative 11 for Custom Menu 6 (CM6Alt11Value)
|  |  | Alternative 12 - Text | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Alternative 12 - Value | Value for alternative 12 for Custom Menu 6 (CM6Alt12Value)
|  |  | Alternative 13 - Text | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Alternative 13 - Value | Value for alternative 13 for Custom Menu 6 (CM6Alt13Value)
|  |  | Alternative 14 - Text | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternative 14 - Value | Value for alternative 14 for Custom Menu 6 (CM6Alt14Value)
|  |  | Alternative 15 - Text | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Alternative 15 - Value | Value for alternative 15 for Custom Menu 6 (CM6Alt15Value)
|  |  | Alternative 16 - Text | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternative 16 - Value | Value for alternative 16 for Custom Menu 6 (CM6Alt16Value)
|  |  | Alternative 17 - Text | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Alternative 17 - Value | Value for alternative 17 for Custom Menu 6 (CM6Alt17Value)
|  |  | Alternative 18 - Text | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Alternative 18 - Value | Value for alternative 18 for Custom Menu 6 (CM6Alt18Value)
|  |  | Alternative 19 - Text | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Alternative 19 - Value | Value for alternative 19 for Custom Menu 6 (CM6Alt19Value)
|  |  | Alternative 20 - Text | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Alternative 20 - Value | Value for alternative 20 for Custom Menu 6 (CM6Alt20Value)
|  |  | Alternative 21 - Text | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Alternative 21 - Value | Value for alternative 21 for Custom Menu 6 (CM6Alt21Value)
Custom menu 7
|  |  | Title | Title for Custom Menu 7 (CM7Title)
|  |  | Current value | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Alternative 1 - Text | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Alternative 1 - Value | Value for alternative 1 for Custom Menu 7 (CM7Alt1Value)
|  |  | Alternative 2 - Text | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Alternative 2 - Value | Value for alternative 2 for Custom Menu 7 (CM7Alt2Value)
|  |  | Alternative 3 - Text | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Alternative 3 - Value | Value for alternative 3 for Custom Menu 7 (CM7Alt3Value)
|  |  | Alternative 4 - Text | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Alternative 4 - Value | Value for alternative 4 for Custom Menu 7 (CM7Alt4Value)
|  |  | Alternative 5 - Text | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Alternative 5 - Value | Value for alternative 5 for Custom Menu 7 (CM7Alt5Value)
|  |  | Alternative 6 - Text | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Alternative 6 - Value | Value for alternative 6 for Custom Menu 7 (CM7Alt6Value)
|  |  | Alternative 7 - Text | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Alternative 7 - Value | Value for alternative 7 for Custom Menu 7 (CM7Alt7Value)
|  |  | Alternative 8 - Text | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Alternative 8 - Value | Value for alternative 8 for Custom Menu 7 (CM7Alt8Value)
|  |  | Alternative 9 - Text | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Alternative 9 - Value | Value for alternative 9 for Custom Menu 7 (CM7Alt9Value)
|  |  | Alternative 10 - Text | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Alternative 10 - Value | Value for alternative 10 for Custom Menu 7 (CM7Alt10Value)
|  |  | Alternative 11 - Text | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Alternative 11 - Value | Value for alternative 11 for Custom Menu 7 (CM7Alt11Value)
|  |  | Alternative 12 - Text | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Alternative 12 - Value | Value for alternative 12 for Custom Menu 7 (CM7Alt12Value)
|  |  | Alternative 13 - Text | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Alternative 13 - Value | Value for alternative 13 for Custom Menu 7 (CM7Alt13Value)
|  |  | Alternative 14 - Text | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Alternative 14 - Value | Value for alternative 14 for Custom Menu 7 (CM7Alt14Value)
|  |  | Alternative 15 - Text | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Alternative 15 - Value | Value for alternative 15 for Custom Menu 7 (CM7Alt15Value)
|  |  | Alternative 16 - Text | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Alternative 16 - Value | Value for alternative 16 for Custom Menu 7 (CM7Alt16Value)
|  |  | Alternative 17 - Text | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Alternative 17 - Value | Value for alternative 17 for Custom Menu 7 (CM7Alt17Value)
|  |  | Alternative 18 - Text | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Alternative 18 - Value | Value for alternative 18 for Custom Menu 7 (CM7Alt18Value)
|  |  | Alternative 19 - Text | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Alternative 19 - Value | Value for alternative 19 for Custom Menu 7 (CM7Alt19Value)
|  |  | Alternative 20 - Text | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Alternative 20 - Value | Value for alternative 20 for Custom Menu 7 (CM7Alt20Value)
|  |  | Alternative 21 - Text | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Alternative 21 - Value | Value for alternative 21 for Custom Menu 7 (CM7Alt21Value)
Custom menu 8
|  |  | Title | Title for Custom Menu 8 (CM8Title)
|  |  | Current value | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Alternative 1 - Text | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Alternative 1 - Value | Value for alternative 1 for Custom Menu 8 (CM8Alt1Value)
|  |  | Alternative 2 - Text | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Alternative 2 - Value | Value for alternative 2 for Custom Menu 8 (CM8Alt2Value)
|  |  | Alternative 3 - Text | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Alternative 3 - Value | Value for alternative 3 for Custom Menu 8 (CM8Alt3Value)
|  |  | Alternative 4 - Text | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Alternative 4 - Value | Value for alternative 4 for Custom Menu 8 (CM8Alt4Value)
|  |  | Alternative 5 - Text | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Alternative 5 - Value | Value for alternative 5 for Custom Menu 8 (CM8Alt5Value)
|  |  | Alternative 6 - Text | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Alternative 6 - Value | Value for alternative 6 for Custom Menu 8 (CM8Alt6Value)
|  |  | Alternative 7 - Text | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Alternative 7 - Value | Value for alternative 7 for Custom Menu 8 (CM8Alt7Value)
|  |  | Alternative 8 - Text | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Alternative 8 - Value | Value for alternative 8 for Custom Menu 8 (CM8Alt8Value)
|  |  | Alternative 9 - Text | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Alternative 9 - Value | Value for alternative 9 for Custom Menu 8 (CM8Alt9Value)
|  |  | Alternative 10 - Text | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Alternative 10 - Value | Value for alternative 10 for Custom Menu 8 (CM8Alt10Value)
|  |  | Alternative 11 - Text | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Alternative 11 - Value | Value for alternative 11 for Custom Menu 8 (CM8Alt11Value)
|  |  | Alternative 12 - Text | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Alternative 12 - Value | Value for alternative 12 for Custom Menu 8 (CM8Alt12Value)
|  |  | Alternative 13 - Text | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Alternative 13 - Value | Value for alternative 13 for Custom Menu 8 (CM8Alt13Value)
|  |  | Alternative 14 - Text | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Alternative 14 - Value | Value for alternative 14 for Custom Menu 8 (CM8Alt14Value)
|  |  | Alternative 15 - Text | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Alternative 15 - Value | Value for alternative 15 for Custom Menu 8 (CM8Alt15Value)
|  |  | Alternative 16 - Text | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Alternative 16 - Value | Value for alternative 16 for Custom Menu 8 (CM8Alt16Value)
|  |  | Alternative 17 - Text | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Alternative 17 - Value | Value for alternative 17 for Custom Menu 8 (CM8Alt17Value)
|  |  | Alternative 18 - Text | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Alternative 18 - Value | Value for alternative 18 for Custom Menu 8 (CM8Alt18Value)
|  |  | Alternative 19 - Text | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Alternative 19 - Value | Value for alternative 19 for Custom Menu 8 (CM8Alt19Value)
|  |  | Alternative 20 - Text | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Alternative 20 - Value | Value for alternative 20 for Custom Menu 8 (CM8Alt20Value)
|  |  | Alternative 21 - Text | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Alternative 21 - Value | Value for alternative 21 for Custom Menu 8 (CM8Alt21Value)
Actuators
On/off outputs
|  |  | Heating hysteresis, room temperature [ºC] | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Cooling hysteresis, room temperature [ºC] | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysteresis, extra zone temperature [ºC] | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Valve exercise
|  |  | Exercise valves | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Heat interval [h] | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Heat 2 interval [h] | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Cool interval [h] | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Cool 2 interval [h] | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Change-over interval [h] | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | 6-way valve interval [h] | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Heat duration [s] | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Heat 2 duration [s] | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Cool duration [s] | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Cool 2 duration [s] | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Change-over duration [s] | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | 6-way valve duration [s] | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analog inputs
Temperature input
|  |  | Filter time [s] | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperature input 0-10V
|  |  | Value at 0 V [°C] | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Value at 10 V [°C] | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2 input
|  |  | Value at 0 V [ppm] | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Value at 10 V [ppm] | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filter time [s] | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Humidity input
|  |  | Value at 0 V [%] | RH at 0 Volt input (RC_RH_0V)
|  |  | Value at 10 V [%] | RH at 10 Volt input (RC_RH_10V)
|  |  | Filter time [s] | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Flow input
|  |  | Value at 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Value at 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filter time [s] | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC input
|  |  | Value at 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Value at 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filter time [s] | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Setpoints
Room setpoints
|  |  | Heating, occupied [°C] | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Cooling, occupied [°C] | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Heating, standby [°C] | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Cooling, standby [°C] | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Heating, unoccupied [°C] | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Cooling, unoccupied [°C] | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Frost protection [°C] | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Setpoint adjustment
|  |  | Max up adjustment [°C] | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Max down adjustment [°C] | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Setpoint adjustment [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Extra zone
|  |  | Extra zone setpoint [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2 setpoint [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Humidity
|  |  | Humidity setpoint [%] | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC setpoint | Setpoint for VOC control (RC_VOCSetpoint)
Controller settings
Room
|  |  | P-band [°C] | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-time [s] | I-time for room PID controller (RC_RoomPIDItime)
Cascade control
|  |  | Control active | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Cascade factor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Max heating temperature [°C] | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min heating temperature [°C] | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Max cooling temperature [°C] | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min cooling temperature [°C] | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Frost protection temperature [°C] | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Extra zone
|  |  | P-band [°C] | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-time [s] | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-band [ppm] | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-time [s] | I-time for CO2 PID controller (RC_CO2PIDItime)
Humidity
|  |  | P-band [%] | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-time [s] | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-band | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-time [s] | I-time for VOC PID controller (RC_VOCPIDItime)
Alarm settings
Room temperature alarm
|  |  | High limit [°C] | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Low limit [°C] | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
CO2 level alarm
|  |  | High limit [ppm] | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Input adjustments
UI1
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Offset adjustment | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Offset adjustment | Offset for input (IoAnaIn_2_offset)
Room temperature
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Offset adjustment | Offset for input (IoAnaIn_5_offset)
Room humidity
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Offset adjustment | Offset for input (IoAnaIn_6_offset)
VOC sensor
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Offset adjustment | Offset for input (IoAnaIn_7_offset)
CO2 sensor
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Offset adjustment | Offset for input (IoAnaIn_8_offset)
Output adjustments
UO1
|  |  | Minimum value | Scale for output (IoAnaOut_1_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_1_max_out)
|  |  | Offset based on full range [-100=-100%, 100=100%] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Minimum value | Scale for output (IoAnaOut_2_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_2_max_out)
|  |  | Offset based on full range [-100=-100%, 100=100%] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Minimum value | Scale for output (IoAnaOut_3_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_3_max_out)
|  |  | Offset based on full range [-100=-100%, 100=100%] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Minimum value | Scale for output (IoAnaOut_4_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_4_max_out)
|  |  | Offset based on full range [-100=-100%, 100=100%] | Offset for output (IoAnaOut_4_offset)
Manual/Auto
Remote input values
Room temperature
|  |  | Remote setting | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Set value [°C] | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Room temperature [°C] | Room temperature (RC_RoomTemp)
Supply air temperature
|  |  | Remote setting | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Set value [°C] | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Supply air temperature [°C] | Supply air temperature (RC_SupplyAirTemp)
Extra zone temperature
|  |  | Remote setting | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Set value [°C] | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Extra zone temperature [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
Change-over temperature
|  |  | Remote setting | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Set value [°C] | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-over temperature [°C] | Changeover temperature (RC_ChangeOverTemp)
Change-over VAV temperature
|  |  | Remote setting | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Set value [°C] | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-over VAV temperature [°C] | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2 level
|  |  | Remote setting | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Set value [ppm] | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2 level [ppm] | Room CO2 level (RC_CO2Level)
Room humidity
|  |  | Remote setting | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Set value [%] | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Room humidity [%] | Relative humidity (RC_Humidity)
Air Flow
|  |  | Remote setting | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Set value | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Air Flow | Air flow (RC_AirFlow)
VOC index
|  |  | Remote setting | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Set value | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC index | VOC index (RC_VOC)
Presence detection
|  |  | Remote setting | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Set value | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Presence detection | Presence indication (RC_Presence)
Open window
|  |  | Remote setting | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Set value | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Open window | Open window indication (RC_DIOpenWindow)
Condensation
|  |  | Remote setting | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Set value | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Condensation | Condensation indication (RC_DICondensation)
External alarm (DI)
|  |  | Remote setting | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Set value | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | External alarm (DI) | Digital input alarm (RC_AlarmDI)
Change-over DI
|  |  | Remote setting | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Set value | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-over DI | Change-over digital input (RC_DIChangeOver)
Change-over VAV DI
|  |  | Remote setting | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Set value | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-over VAV DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Manual/Auto
Controller state
|  |  | Controller state | Current state (RC_ControllerState)
|  |  | Remote state setting | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Shutdown | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Forced ventilation | Set controller in Bypass state (RC_ControllerStateSetBypass)
Fan control source
|  |  | Fan control source | Fan speed setting (RC_FanSelect)
Heating output
|  |  | Mode | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Set value [%] | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Heating output [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Mode | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Heating output | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Heating 2 output
|  |  | Mode | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Set value [%] | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Heating 2 output [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Mode | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Heating 2 output | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Cooling output
|  |  | Mode | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Set value [%] | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Cooling output [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Mode | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Cooling output | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Cooling 2 output
|  |  | Mode | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Set value [%] | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Cooling 2 output [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Mode | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Cooling 2 output | Room control Cool2 output digital (RC_RoomCool2OutputDO)
VAV output
|  |  | Mode | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Set value [%] | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | VAV output [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
VAV 2 output
|  |  | Mode | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Set value [%] | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | VAV 2 output [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Change-over output
|  |  | Mode | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Set value [%] | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Change-over output [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Change-over VAV output
|  |  | Mode | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Set value [%] | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Change-over VAV output [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
6-way valve output
|  |  | Mode | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Mode | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Set value [%] | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | 6-way valve output [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Extra zone output
|  |  | Mode | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Set value [%] | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Extra zone output | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC Fan control
|  |  | Mode | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Set value [%] | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC Fan control [%] | Current EC fan speed (RC_ECFanSpeed)
CO2 control output
|  |  | Mode | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Set value [%] | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | CO2 control output [%] | CO2 control analog out (RC_CO2ControlAO)
Humidify control output
|  |  | Mode | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Set value [%] | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Humidify control output [%] | Humidify analog out (RC_HumidifyOutputAO)
Dehumidify control output
|  |  | Mode | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Set value [%] | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Dehumidify control output [%] | Dehumidify analog out (RC_DehumidifyOutputAO)
VOC control output
|  |  | Mode | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Set value [%] | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | VOC control output [%] | VOC control analog out (RC_VOCControlAO)
Extra zone active output
|  |  | Mode | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Extra zone active output | Extra Zone active (RC_ExtraZoneActive)
Forced ventilation output
|  |  | Mode | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Forced ventilation output | Forced ventilation output (RC_ForcedVentDO)
Hardware control
UO1
|  |  | UO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Mode | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Set value | Override value (IoDo_1_override)
UO2
|  |  | UO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_2_override)
|  |  | UO2: | Value set for output (IoDo_2_value)
|  |  | Mode | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Set value | Override value (IoDo_2_override)
AO1
|  |  | AO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_3_override)
AO2
|  |  | AO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Set value | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Set value | Override value (IoAnaIn_2_override)
CO2 sensor calibration
|  |  | Enable automatic self calibration | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Automatic self calibration baseline [ppm] [ppm] | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | Run CO2 sensor forced recalibration | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | Reference CO2 level for forced recalibration [ppm] [ppm] | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Last forced recalibration offset (-9999 = Error) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | Reset CO2 sensor | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Relay output
|  |  | Relay state | Value set for output (IoDo_3_value)
|  |  | Mode | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Set value | Override value (IoDo_3_override)
PIR sensor
|  |  | PIR sensor | Filtered value from sensor (IoDiIn_4_value)
|  |  | Mode | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Set value | Override value (IoDiIn_4_override)
Device
Device ID
Device ID
|  |  | Name | (ControllerName)
|  |  | Description | Controller description (ControllerDescription)
|  |  | Location | Controller location (ControllerLocation)
|  |  | Project | (ControllerProject)
Communication
Port settings
|  |  | Port 1 function | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Port 1 baudrate | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Port 1 parity | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbus address | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | BACnet MSTP address | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | MSTP max master address | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet device ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet device object name | BACnet device object name (BACnetDeviceObjectName)
|  |  | Password | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth function | Function for BLE button (BleButtonMode)
|  |  | Turn off after [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | BLE transmission power | BLE TX power level (ble_power)
Communication fail
|  |  | Fail action | Offline function (RC_OfflineFunction)
|  |  | Timeout [s] | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Fallback state | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Reset
Reset
|  |  | Restart controller | Write to this register will trigger resets with different reset reasons (product_reset)
Non volatile storage
Non volatile storage
|  |  | Disable non volatile storage | Set to 1 to disable storage in non volatile memory (disable_nv_storage)

## da
RCX-2.1-1-01 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Oversigt
System
|  |  | Controller | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbus adresse | Active Modbus unit ID (ModbusUnitID)
|  |  | BACnet MSTP adresse | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet enheds ID | BACnet device ID (BACnetDeviceID)
|  |  | Sum alarm | Sum Alarm (RC_SumAlarm)
Rum
|  |  | Controller tilstand | Current state (RC_ControllerState)
|  |  | Tilstand | Current controller mode (RC_ControllerMode)
|  |  | Rumtemperatur [°C] | Room temperature (RC_RoomTemp)
|  |  | Tilluft temperatur [°C] | Supply air temperature (RC_SupplyAirTemp)
|  |  | Rum sætpunkt [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Sætpunkts justering [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC ventilator hastighed [%] | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2 niveau [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Rum fugtighed [%] | Relative humidity (RC_Humidity)
|  |  | VOC indeks | VOC index (RC_VOC)
|  |  | Tilstedeværelses detektering | Presence indication (RC_Presence)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Ekstra zone
|  |  | Ekstra zone temperatur [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Ekstra zone sætpunkt [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Ekstra zone aktiv udgang | Extra Zone active (RC_ExtraZoneActive)
Aktuel værdi
Rum kontrol sekvens
|  |  | Sekvens 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sekvens 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sekvens 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Aktuel værdi
|  |  | Tilstand | Current controller mode (RC_ControllerMode)
|  |  | Rumtemperatur [°C] | Room temperature (RC_RoomTemp)
|  |  | Rum sætpunkt [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Sætpunkts justering [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Varme behov [%] | Room PID heat output (RC_PIDHeatDemand)
|  |  | Køle behov [%] | Room PID cool output (RC_PIDCoolDemand)
|  |  | Varme udgang [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Varme 2 udgang [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Køling udgang [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Køling 2 udgang [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | VAV udgang [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | VAV 2 udgang [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-over temperatur | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-over tilstand | Change-over status (RC_ChangeOverState)
|  |  | Change-over udgang [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-over temperatur | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-over VAV tilstand | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Change-over VAV udgang [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | 6-vejsventil udgang [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2 niveau [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2 sætpunkt [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Relæ udgang
|  |  | Relæ status | Value set for output (IoDo_3_value)
Indgange/udgange
Universal indgange
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universal udgange
|  |  | UO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analoge udgange
|  |  | AO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Interne følere
|  |  | Rumtemperatur [°C] | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2 føler [ppm] | Filtered value from sensor (IoAnaIn_8_value)
|  |  | RH føler [%] | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC føler | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR føler | Filtered value from sensor (IoDiIn_4_value)
Alarmer
Alarmer
|  |  | Sum alarm | Sum Alarm (RC_SumAlarm)
|  |  | Føler fejl | Sensor error alarm (RC_AlarmSensorError)
|  |  | Høj rumtemperatur | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Lav rumtemperatur | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | Højt CO2 niveau | High CO2 alarm (RC_AlarmCO2High)
|  |  | Ekstern alarm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Udgang i manuel tilstand | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Temperatur føler fejl kode | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Fugtighed føler fejl kode | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | VOC føler fejl kode | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | CO2 føler fejl kode | Detailed fault description (IoAnaIn_8_errorFlags)
Om
Enhed ID
|  |  | Serie nummer | (SerialNumberString)
|  |  | Navn | (ControllerName)
|  |  | Beskrivelse | Controller description (ControllerDescription)
|  |  | Lokation | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Brugerdefinerede menuer
Brugerdefineret menu 1
|  |  | Titel | Title for Custom Menu 1 (CM1Title)
|  |  | Aktuel værdi | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Nuværende alternativ | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Nuværende alternativ | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Nuværende alternativ | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Nuværende alternativ | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Nuværende alternativ | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Nuværende alternativ | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Nuværende alternativ | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Nuværende alternativ | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Nuværende alternativ | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Nuværende alternativ | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Nuværende alternativ | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Nuværende alternativ | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Nuværende alternativ | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Nuværende alternativ | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Nuværende alternativ | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Nuværende alternativ | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Nuværende alternativ | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Nuværende alternativ | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Nuværende alternativ | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Nuværende alternativ | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Nuværende alternativ | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Nuværende alternativ indeks | Current alternative for Custom Menu 1 (CM1CurrentAlt)
Brugerdefineret menu 2
|  |  | Titel | Title for Custom Menu 2 (CM2Title)
|  |  | Aktuel værdi | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Nuværende alternativ | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Nuværende alternativ | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Nuværende alternativ | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Nuværende alternativ | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Nuværende alternativ | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Nuværende alternativ | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Nuværende alternativ | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Nuværende alternativ | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Nuværende alternativ | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Nuværende alternativ | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Nuværende alternativ | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Nuværende alternativ | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Nuværende alternativ | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Nuværende alternativ | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Nuværende alternativ | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Nuværende alternativ | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Nuværende alternativ | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Nuværende alternativ | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Nuværende alternativ | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Nuværende alternativ | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Nuværende alternativ | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Nuværende alternativ indeks | Current alternative for Custom Menu 2 (CM2CurrentAlt)
Brugerdefineret menu 3
|  |  | Titel | Title for Custom Menu 3 (CM3Title)
|  |  | Aktuel værdi | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Nuværende alternativ | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Nuværende alternativ | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Nuværende alternativ | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Nuværende alternativ | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Nuværende alternativ | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Nuværende alternativ | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Nuværende alternativ | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Nuværende alternativ | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Nuværende alternativ | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Nuværende alternativ | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Nuværende alternativ | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Nuværende alternativ | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Nuværende alternativ | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Nuværende alternativ | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Nuværende alternativ | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Nuværende alternativ | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Nuværende alternativ | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Nuværende alternativ | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Nuværende alternativ | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Nuværende alternativ | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Nuværende alternativ | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Nuværende alternativ indeks | Current alternative for Custom Menu 3 (CM3CurrentAlt)
Brugerdefineret menu 4
|  |  | Titel | Title for Custom Menu 4 (CM4Title)
|  |  | Aktuel værdi | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Nuværende alternativ | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Nuværende alternativ | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Nuværende alternativ | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Nuværende alternativ | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Nuværende alternativ | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Nuværende alternativ | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Nuværende alternativ | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Nuværende alternativ | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Nuværende alternativ | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Nuværende alternativ | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Nuværende alternativ | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Nuværende alternativ | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Nuværende alternativ | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Nuværende alternativ | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Nuværende alternativ | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Nuværende alternativ | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Nuværende alternativ | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Nuværende alternativ | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Nuværende alternativ | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Nuværende alternativ | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Nuværende alternativ | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Nuværende alternativ indeks | Current alternative for Custom Menu 4 (CM4CurrentAlt)
Brugerdefineret menu 5
|  |  | Titel | Title for Custom Menu 5 (CM5Title)
|  |  | Aktuel værdi | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Nuværende alternativ | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Nuværende alternativ | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Nuværende alternativ | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Nuværende alternativ | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Nuværende alternativ | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Nuværende alternativ | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Nuværende alternativ | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Nuværende alternativ | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Nuværende alternativ | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Nuværende alternativ | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Nuværende alternativ | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Nuværende alternativ | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Nuværende alternativ | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Nuværende alternativ | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Nuværende alternativ | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Nuværende alternativ | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Nuværende alternativ | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Nuværende alternativ | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Nuværende alternativ | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Nuværende alternativ | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Nuværende alternativ | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Nuværende alternativ indeks | Current alternative for Custom Menu 5 (CM5CurrentAlt)
Brugerdefineret menu 6
|  |  | Titel | Title for Custom Menu 6 (CM6Title)
|  |  | Aktuel værdi | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Nuværende alternativ | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Nuværende alternativ | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Nuværende alternativ | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Nuværende alternativ | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Nuværende alternativ | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Nuværende alternativ | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Nuværende alternativ | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Nuværende alternativ | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Nuværende alternativ | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Nuværende alternativ | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Nuværende alternativ | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Nuværende alternativ | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Nuværende alternativ | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Nuværende alternativ | Text for alternative 14 for Custom Menu 6 (CM6Alt14Text)
|  |  | Nuværende alternativ | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Nuværende alternativ | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Nuværende alternativ | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Nuværende alternativ | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Nuværende alternativ | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Nuværende alternativ | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Nuværende alternativ | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Nuværende alternativ indeks | Current alternative for Custom Menu 6 (CM6CurrentAlt)
Brugerdefineret menu 7
|  |  | Titel | Title for Custom Menu 7 (CM7Title)
|  |  | Aktuel værdi | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Nuværende alternativ | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Nuværende alternativ | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Nuværende alternativ | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Nuværende alternativ | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Nuværende alternativ | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Nuværende alternativ | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Nuværende alternativ | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Nuværende alternativ | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Nuværende alternativ | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Nuværende alternativ | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Nuværende alternativ | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Nuværende alternativ | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Nuværende alternativ | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Nuværende alternativ | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Nuværende alternativ | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Nuværende alternativ | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Nuværende alternativ | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Nuværende alternativ | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Nuværende alternativ | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Nuværende alternativ | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Nuværende alternativ | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Nuværende alternativ indeks | Current alternative for Custom Menu 7 (CM7CurrentAlt)
Brugerdefineret menu 8
|  |  | Titel | Title for Custom Menu 8 (CM8Title)
|  |  | Aktuel værdi | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Nuværende alternativ | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Nuværende alternativ | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Nuværende alternativ | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Nuværende alternativ | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Nuværende alternativ | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Nuværende alternativ | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Nuværende alternativ | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Nuværende alternativ | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Nuværende alternativ | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Nuværende alternativ | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Nuværende alternativ | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Nuværende alternativ | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Nuværende alternativ | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Nuværende alternativ | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Nuværende alternativ | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Nuværende alternativ | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Nuværende alternativ | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Nuværende alternativ | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Nuværende alternativ | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Nuværende alternativ | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Nuværende alternativ | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Nuværende alternativ indeks | Current alternative for Custom Menu 8 (CM8CurrentAlt)
Konfiguration
Kontrolfunktioner
Rum kontrol sekvens
|  |  | Sekvens 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sekvens 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sekvens 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Varme
|  |  | Maks. grænse [%] | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min. grænse [%] | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Ventilator fra- forsinkelse for elektrisk varmelegeme | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Følg change-over tilstand | Heat1 included in change-over function (RC_Heat1InChangeOver)
Varme 2
|  |  | Maks. grænse [%] | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min. grænse [%] | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Ventilator fra- forsinkelse for elektrisk varmelegeme | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Følg change-over tilstand | Heat2 included in change-over function (RC_Heat2InChangeOver)
Køle
|  |  | Maks. grænse [%] | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min. grænse [%] | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Indstil til maks. ved tvungen ventilationstilstand | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Slå udgang fra, når ventilator er slukket | Turn off Cool1 output when the fan is off (RC_Cool1OffWhenFanIsOff)
|  |  | Følg change-over tilstand | Cool1 included in change-over function (RC_Cool1InChangeOver)
Køle 2
|  |  | Maks. grænse [%] | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min. grænse [%] | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Indstil til maks. ved tvungen ventilationstilstand | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Slå udgang fra, når ventilator er slukket | Turn off Cool2 output when the fan is off (RC_Cool2OffWhenFanIsOff)
|  |  | Følg change-over tilstand | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Maks. grænse [%] | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min. grænse, fra [%] | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min. grænse, unoccupied [%] | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min. grænse, standby [%] | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min. grænse, occupied [%] | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min. grænse, tvungen ventilation [%] | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Indstil til maks. ved tvungen ventilationstilstand | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Maks. grænse ved varme [%] | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Følg change-over tilstand | VAV1 included in change-over function (RC_VAV1InChangeOver)
|  |  | Start VAV, når forrige kølingssekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Start VAV, når forrige varmesekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VAV 2
|  |  | Maks. grænse [%] | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min. grænse, fra [%] | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min. grænse, unoccupied [%] | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min. grænse, standby [%] | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min. grænse, occupied [%] | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min. grænse, tvungen ventilation [%] | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Indstil til maks. ved tvungen ventilationstilstand | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Maks. grænse ved varme [%] | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Følg change-over tilstand | VAV2 included in change-over function (RC_VAV2InChangeOver)
|  |  | Start VAV, når forrige kølingssekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Start VAV, når forrige varmesekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VAV styre kilde
|  |  | Køle behov | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2 niveau | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC indeks | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Fugtighed | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Maks. grænse [%] | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min. grænse [%] | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Tilstand | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-over temperatur [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Varme hysterese [°C] | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Køling hysterese [°C] | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Ventil forsinkelsestid [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over VAV
|  |  | Maks. grænse [%] | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min. grænse, fra [%] | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min. grænse, unoccupied [%] | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min. grænse, standby [%] | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min. grænse, occupied [%] | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min. grænse, tvungen ventilation [%] | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Indstil til maks. ved tvungen ventilationstilstand | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Tilstand | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-over temperatur [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Varme hysterese [°C] | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Køling hysterese [°C] | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Ventil forsinkelsestid [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
|  |  | Start VAV, når forrige kølingssekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Start VAV, når forrige varmesekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
6-vejsventil
|  |  | Sekv. 1 helt åben [V] | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Sekv. 1 start åbning [V] | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Sekv. 2 helt åben [V] | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Sekv. 2 start åbning [V] | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Midterpunkt [V] | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Midterpunkt hysterese [%] | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Sekvensrækkefølge | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Følg change-over tilstand | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Controller tilstand
|  |  | Forudindstillet tilstand | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Nedluknings tilstand | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Vindue åbent tilstand | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Tid i tvungen ventilations tilstand [min] | Bypass time (minutes) (RC_BypassTime)
Tvungen ventilation
|  |  | Aktiv, når | Forced ventilation function (RC_ForcedVentMode)
|  |  | Start grænse [%] | Forced ventilation start limit (RC_ForcedVentStartLimit)
Tilstedeværelses detektering
|  |  | Tilstedeværelses tilstand | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Aktiv forsinkelse [min] | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Inaktiv forsinkelse [min] | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2 aktivering | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2 niveau [ppm] | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2 hysterese [ppm] | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Brug intern PIR til tilstedeværelse | Use internal PIR sensor for presence detection (RC_PIRPresence)
Ekstra zone
Ekstra zone
|  |  | Ekstra zone funktion | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Deaktiveret under tilstand | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Deaktiver, hvis hovedzonetilstand afviger fra funktion | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min. grænse [%] | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Maks. grænse [%] | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Indgange/udgange
Universal indgange
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universal udgange
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | UO1 periode termisk ventil [s] | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | UO1 styresignal | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | UO2 periode termisk ventil [s] | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | UO2 styresignal | Unit converter (IoAnaOut_2_unit)
Analoge udgange
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO1 styresignal | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | AO2 styresignal | Unit converter (IoAnaOut_4_unit)
Ventilator kontrol
Ventilator styre kilde
|  |  | Rum kontroller | Select fan control mode (RC_FanControlMode)
|  |  | CO2 niveau | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Fugtighed | Fan is controlled by humidity output (RC_FanControlHumidity)
EC ventilator styring
|  |  | Hastighed uden behov | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Fra under behov [%] | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysterese for reduktion af ventilator hastighed [%] | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Start hastighed [%] | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Maks. hastighed i automatisk tilstand [%] | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Tvungen ventilation hastighed | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Tvungen ventilation hastighed [%] | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Hastighed 1 udgang [%] | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Hastighed 2 udgang [%] | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Hastighed 3 udgang [%] | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Skimmel beskyttelse | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Ventilator kickstart
|  |  | Kickstart-tid [s] | Fan kick start time (RC_FanKickStartTime)
Ventilator fra- forsinkelse
|  |  | Fra forsinkelses tid [s] | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Min. hastighed | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Ventilator boost
|  |  | Tilstand | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Boost-tid [s] | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-bånd | Fan boost P band (RC_FanBoostPBand)
Display og menuer
Display
|  |  | Start skærm | What to display during device startup (DisplayStartupMode)
|  |  | Visning tilstand | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Sætpunkt tilstand | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | Afrund CO2 værdi til nærmeste | Min step for CO2 value (RC_CO2Step)
|  |  | Lysstyrke fuld [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Dæmpnings timeout, 0 = Altid fuld [s] | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Lysstyrke dæmpet [%] | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Fra timeout, 0 = Aldrig Fra [s] | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Inaktivt display
|  |  | Temperatur/setpunkt | Show temperature/setpoint in idle view (App_IdleViewTemperature)
|  |  | CO2 niveau | Show CO2 value in idle view (App_IdleViewCO2)
|  |  | Rum fugtighed | Show humidity in idle view (App_IdleViewHumidity)
|  |  | VOC indeks | Show VOC in idle view (App_IdleViewVOC)
|  |  | Controller tilstand | Show mode in idle view (App_IdleViewMode)
Menu
|  |  | Setpunkts justeringsside | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Tilstand menu side | Enable Mode menu page (App_EnableMenuMode)
|  |  | Change-over menu side | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Ventilator menu side | Enable Fan menu page (App_EnableMenuFan)
|  |  | Tvungen ventilation menu side | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Tvungen ventilation forlænget drift | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Siden Temperatur/setpunkt | Enable Temperature menu page (App_EnableMenuTemp)
|  |  | Fugtighed menu side | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | CO2 menu side | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | VOC menu side | Enable VOC menu page (App_EnableMenuVOC)
Display rækkefølge
|  |  | Display position 1 | Display position 1 (DisplayPosition1)
|  |  | Display position 2 | Display position 2 (DisplayPosition2)
|  |  | Display position 3 | Display position 3 (DisplayPosition3)
|  |  | Display position 4 | Display position 4 (DisplayPosition4)
|  |  | Display position 5 | Display position 5 (DisplayPosition5)
|  |  | Display position 6 | Display position 6 (DisplayPosition6)
|  |  | Display position 7 | Display position 7 (DisplayPosition7)
|  |  | Display position 8 | Display position 8 (DisplayPosition8)
|  |  | Display position 9 | Display position 9 (DisplayPosition9)
|  |  | Display position 10 | Display position 10 (DisplayPosition10)
|  |  | Display position 11 | Display position 11 (DisplayPosition11)
|  |  | Display position 12 | Display position 12 (DisplayPosition12)
Tilpassede menuindstillinger
|  |  | Brugerdefineret menu 1 | Enable Custom Menu 1 (CM1Enabled)
|  |  | Brugerdefineret menu 2 | Enable Custom Menu 2 (CM2Enabled)
|  |  | Brugerdefineret menu 3 | Enable Custom Menu 3 (CM3Enabled)
|  |  | Brugerdefineret menu 4 | Enable Custom Menu 4 (CM4Enabled)
|  |  | Brugerdefineret menu 5 | Enable Custom Menu 5 (CM5Enabled)
|  |  | Brugerdefineret menu 6 | Enable Custom Menu 6 (CM6Enabled)
|  |  | Brugerdefineret menu 7 | Enable Custom Menu 7 (CM7Enabled)
|  |  | Brugerdefineret menu 8 | Enable Custom Menu 8 (CM8Enabled)
Menuvalg muligheder
|  |  | Menu titel tekst | Mode menu title (App_ModeMenuTitle)
|  |  | Tilstand Fra aktiveret | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Tilstand unoccupied aktiveret | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Tilstand standby aktiveret | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Tilstand occupied aktiveret | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Tilstand tvungen ventilation aktiveret | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Tilstand Fra tekst | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Tilstand unoccupied tekst | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Tilstand standby tekst | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Tilstand occupied tekst | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Tilstand tvungen ventilation tekst | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Tilstand auto tekst | Mode menu Auto state text (App_ModeMenuAutoText)
Change-over menuvalg muligheder
|  |  | Menu titel tekst | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | Tilstand varme aktiveret | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | Tilstand køling aktiveret | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | Tilstand auto aktiveret | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | Tilstand varme tekst | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | Tilstand køling tekst | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | Tilstand auto tekst | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
LED indikation
|  |  | Lysstyrke [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 LED indikation | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Gul LED CO2 niveau [ppm] | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Rød LED CO2 niveau [ppm] | CO2 level for red led (RC_CO2LevelRed)
Brugerdefinerede tekster
|  |  | Visning tilstand | When to show the custom text (rt_text_visability)
|  |  | Display tilstand | Single or dual row text in display (rt_text_mode)
|  |  | Rul-tilstand | Scroll mode (rt_text_display_scroll_mode)
|  |  | Skrifttype | What font to use for the display text (rt_text_font)
|  |  | Rul forsinkelse [ms] | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Bruger defineret tekst timer værdi [s] | Time to show the custom text (rt_text_timeleft)
|  |  | Brugerdefineret tekst række 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Brugerdefineret tekst række 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Brugerdefineret tekst 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Brugerdefineret tekst 2 | String to show on row 2 in the display (rt_text_row_2)
Brugerdefinerede menuer
Brugerdefineret menu 1
|  |  | Titel | Title for Custom Menu 1 (CM1Title)
|  |  | Aktuel værdi | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Alternativ 1 – Tekst | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Alternativ 1 – Værdi | Value for alternative 1 for Custom Menu 1 (CM1Alt1Value)
|  |  | Alternativ 2 – Tekst | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Alternativ 2 – Værdi | Value for alternative 2 for Custom Menu 1 (CM1Alt2Value)
|  |  | Alternativ 3 – Tekst | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Alternativ 3 – Værdi | Value for alternative 3 for Custom Menu 1 (CM1Alt3Value)
|  |  | Alternativ 4 – Tekst | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Alternativ 4 – Værdi | Value for alternative 4 for Custom Menu 1 (CM1Alt4Value)
|  |  | Alternativ 5 – Tekst | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Alternativ 5 – Værdi | Value for alternative 5 for Custom Menu 1 (CM1Alt5Value)
|  |  | Alternativ 6 – Tekst | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Alternativ 6 – Værdi | Value for alternative 6 for Custom Menu 1 (CM1Alt6Value)
|  |  | Alternativ 7 – Tekst | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Alternativ 7 – Værdi | Value for alternative 7 for Custom Menu 1 (CM1Alt7Value)
|  |  | Alternativ 8 – Tekst | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Alternativ 8 – Værdi | Value for alternative 8 for Custom Menu 1 (CM1Alt8Value)
|  |  | Alternativ 9 – Tekst | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Alternativ 9 – Værdi | Value for alternative 9 for Custom Menu 1 (CM1Alt9Value)
|  |  | Alternativ 10 – Tekst | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Alternativ 10 – Værdi | Value for alternative 10 for Custom Menu 1 (CM1Alt10Value)
|  |  | Alternativ 11 – Tekst | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Alternativ 11 – Værdi | Value for alternative 11 for Custom Menu 1 (CM1Alt11Value)
|  |  | Alternativ 12 – Tekst | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Alternativ 12 – Værdi | Value for alternative 12 for Custom Menu 1 (CM1Alt12Value)
|  |  | Alternativ 13 – Tekst | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Alternativ 13 – Værdi | Value for alternative 13 for Custom Menu 1 (CM1Alt13Value)
|  |  | Alternativ 14 – Tekst | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Alternativ 14 – Værdi | Value for alternative 14 for Custom Menu 1 (CM1Alt14Value)
|  |  | Alternativ 15 – Tekst | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Alternativ 15 – Værdi | Value for alternative 15 for Custom Menu 1 (CM1Alt15Value)
|  |  | Alternativ 16 – Tekst | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Alternativ 16 – Værdi | Value for alternative 16 for Custom Menu 1 (CM1Alt16Value)
|  |  | Alternativ 17 – Tekst | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Alternativ 17 – Værdi | Value for alternative 17 for Custom Menu 1 (CM1Alt17Value)
|  |  | Alternativ 18 – Tekst | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Alternativ 18 – Værdi | Value for alternative 18 for Custom Menu 1 (CM1Alt18Value)
|  |  | Alternativ 19 – Tekst | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Alternativ 19 – Værdi | Value for alternative 19 for Custom Menu 1 (CM1Alt19Value)
|  |  | Alternativ 20 – Tekst | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Alternativ 20 – Værdi | Value for alternative 20 for Custom Menu 1 (CM1Alt20Value)
|  |  | Alternativ 21 – Tekst | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Alternativ 21 – Værdi | Value for alternative 21 for Custom Menu 1 (CM1Alt21Value)
Brugerdefineret menu 2
|  |  | Titel | Title for Custom Menu 2 (CM2Title)
|  |  | Aktuel værdi | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Alternativ 1 – Tekst | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Alternativ 1 – Værdi | Value for alternative 1 for Custom Menu 2 (CM2Alt1Value)
|  |  | Alternativ 2 – Tekst | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Alternativ 2 – Værdi | Value for alternative 2 for Custom Menu 2 (CM2Alt2Value)
|  |  | Alternativ 3 – Tekst | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Alternativ 3 – Værdi | Value for alternative 3 for Custom Menu 2 (CM2Alt3Value)
|  |  | Alternativ 4 – Tekst | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Alternativ 4 – Værdi | Value for alternative 4 for Custom Menu 2 (CM2Alt4Value)
|  |  | Alternativ 5 – Tekst | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Alternativ 5 – Værdi | Value for alternative 5 for Custom Menu 2 (CM2Alt5Value)
|  |  | Alternativ 6 – Tekst | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Alternativ 6 – Værdi | Value for alternative 6 for Custom Menu 2 (CM2Alt6Value)
|  |  | Alternativ 7 – Tekst | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Alternativ 7 – Værdi | Value for alternative 7 for Custom Menu 2 (CM2Alt7Value)
|  |  | Alternativ 8 – Tekst | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Alternativ 8 – Værdi | Value for alternative 8 for Custom Menu 2 (CM2Alt8Value)
|  |  | Alternativ 9 – Tekst | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Alternativ 9 – Værdi | Value for alternative 9 for Custom Menu 2 (CM2Alt9Value)
|  |  | Alternativ 10 – Tekst | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Alternativ 10 – Værdi | Value for alternative 10 for Custom Menu 2 (CM2Alt10Value)
|  |  | Alternativ 11 – Tekst | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Alternativ 11 – Værdi | Value for alternative 11 for Custom Menu 2 (CM2Alt11Value)
|  |  | Alternativ 12 – Tekst | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Alternativ 12 – Værdi | Value for alternative 12 for Custom Menu 2 (CM2Alt12Value)
|  |  | Alternativ 13 – Tekst | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Alternativ 13 – Værdi | Value for alternative 13 for Custom Menu 2 (CM2Alt13Value)
|  |  | Alternativ 14 – Tekst | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Alternativ 14 – Værdi | Value for alternative 14 for Custom Menu 2 (CM2Alt14Value)
|  |  | Alternativ 15 – Tekst | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Alternativ 15 – Værdi | Value for alternative 15 for Custom Menu 2 (CM2Alt15Value)
|  |  | Alternativ 16 – Tekst | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Alternativ 16 – Værdi | Value for alternative 16 for Custom Menu 2 (CM2Alt16Value)
|  |  | Alternativ 17 – Tekst | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Alternativ 17 – Værdi | Value for alternative 17 for Custom Menu 2 (CM2Alt17Value)
|  |  | Alternativ 18 – Tekst | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Alternativ 18 – Værdi | Value for alternative 18 for Custom Menu 2 (CM2Alt18Value)
|  |  | Alternativ 19 – Tekst | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Alternativ 19 – Værdi | Value for alternative 19 for Custom Menu 2 (CM2Alt19Value)
|  |  | Alternativ 20 – Tekst | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Alternativ 20 – Værdi | Value for alternative 20 for Custom Menu 2 (CM2Alt20Value)
|  |  | Alternativ 21 – Tekst | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Alternativ 21 – Værdi | Value for alternative 21 for Custom Menu 2 (CM2Alt21Value)
Brugerdefineret menu 3
|  |  | Titel | Title for Custom Menu 3 (CM3Title)
|  |  | Aktuel værdi | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Alternativ 1 – Tekst | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Alternativ 1 – Værdi | Value for alternative 1 for Custom Menu 3 (CM3Alt1Value)
|  |  | Alternativ 2 – Tekst | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Alternativ 2 – Værdi | Value for alternative 2 for Custom Menu 3 (CM3Alt2Value)
|  |  | Alternativ 3 – Tekst | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Alternativ 3 – Værdi | Value for alternative 3 for Custom Menu 3 (CM3Alt3Value)
|  |  | Alternativ 4 – Tekst | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Alternativ 4 – Værdi | Value for alternative 4 for Custom Menu 3 (CM3Alt4Value)
|  |  | Alternativ 5 – Tekst | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Alternativ 5 – Værdi | Value for alternative 5 for Custom Menu 3 (CM3Alt5Value)
|  |  | Alternativ 6 – Tekst | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Alternativ 6 – Værdi | Value for alternative 6 for Custom Menu 3 (CM3Alt6Value)
|  |  | Alternativ 7 – Tekst | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Alternativ 7 – Værdi | Value for alternative 7 for Custom Menu 3 (CM3Alt7Value)
|  |  | Alternativ 8 – Tekst | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Alternativ 8 – Værdi | Value for alternative 8 for Custom Menu 3 (CM3Alt8Value)
|  |  | Alternativ 9 – Tekst | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Alternativ 9 – Værdi | Value for alternative 9 for Custom Menu 3 (CM3Alt9Value)
|  |  | Alternativ 10 – Tekst | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Alternativ 10 – Værdi | Value for alternative 10 for Custom Menu 3 (CM3Alt10Value)
|  |  | Alternativ 11 – Tekst | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Alternativ 11 – Værdi | Value for alternative 11 for Custom Menu 3 (CM3Alt11Value)
|  |  | Alternativ 12 – Tekst | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Alternativ 12 – Værdi | Value for alternative 12 for Custom Menu 3 (CM3Alt12Value)
|  |  | Alternativ 13 – Tekst | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Alternativ 13 – Værdi | Value for alternative 13 for Custom Menu 3 (CM3Alt13Value)
|  |  | Alternativ 14 – Tekst | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Alternativ 14 – Værdi | Value for alternative 14 for Custom Menu 3 (CM3Alt14Value)
|  |  | Alternativ 15 – Tekst | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Alternativ 15 – Værdi | Value for alternative 15 for Custom Menu 3 (CM3Alt15Value)
|  |  | Alternativ 16 – Tekst | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Alternativ 16 – Værdi | Value for alternative 16 for Custom Menu 3 (CM3Alt16Value)
|  |  | Alternativ 17 – Tekst | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Alternativ 17 – Værdi | Value for alternative 17 for Custom Menu 3 (CM3Alt17Value)
|  |  | Alternativ 18 – Tekst | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Alternativ 18 – Værdi | Value for alternative 18 for Custom Menu 3 (CM3Alt18Value)
|  |  | Alternativ 19 – Tekst | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Alternativ 19 – Værdi | Value for alternative 19 for Custom Menu 3 (CM3Alt19Value)
|  |  | Alternativ 20 – Tekst | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Alternativ 20 – Værdi | Value for alternative 20 for Custom Menu 3 (CM3Alt20Value)
|  |  | Alternativ 21 – Tekst | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Alternativ 21 – Værdi | Value for alternative 21 for Custom Menu 3 (CM3Alt21Value)
Brugerdefineret menu 4
|  |  | Titel | Title for Custom Menu 4 (CM4Title)
|  |  | Aktuel værdi | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Alternativ 1 – Tekst | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Alternativ 1 – Værdi | Value for alternative 1 for Custom Menu 4 (CM4Alt1Value)
|  |  | Alternativ 2 – Tekst | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Alternativ 2 – Værdi | Value for alternative 2 for Custom Menu 4 (CM4Alt2Value)
|  |  | Alternativ 3 – Tekst | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Alternativ 3 – Værdi | Value for alternative 3 for Custom Menu 4 (CM4Alt3Value)
|  |  | Alternativ 4 – Tekst | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Alternativ 4 – Værdi | Value for alternative 4 for Custom Menu 4 (CM4Alt4Value)
|  |  | Alternativ 5 – Tekst | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Alternativ 5 – Værdi | Value for alternative 5 for Custom Menu 4 (CM4Alt5Value)
|  |  | Alternativ 6 – Tekst | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Alternativ 6 – Værdi | Value for alternative 6 for Custom Menu 4 (CM4Alt6Value)
|  |  | Alternativ 7 – Tekst | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Alternativ 7 – Værdi | Value for alternative 7 for Custom Menu 4 (CM4Alt7Value)
|  |  | Alternativ 8 – Tekst | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Alternativ 8 – Værdi | Value for alternative 8 for Custom Menu 4 (CM4Alt8Value)
|  |  | Alternativ 9 – Tekst | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Alternativ 9 – Værdi | Value for alternative 9 for Custom Menu 4 (CM4Alt9Value)
|  |  | Alternativ 10 – Tekst | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Alternativ 10 – Værdi | Value for alternative 10 for Custom Menu 4 (CM4Alt10Value)
|  |  | Alternativ 11 – Tekst | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Alternativ 11 – Værdi | Value for alternative 11 for Custom Menu 4 (CM4Alt11Value)
|  |  | Alternativ 12 – Tekst | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Alternativ 12 – Værdi | Value for alternative 12 for Custom Menu 4 (CM4Alt12Value)
|  |  | Alternativ 13 – Tekst | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Alternativ 13 – Værdi | Value for alternative 13 for Custom Menu 4 (CM4Alt13Value)
|  |  | Alternativ 14 – Tekst | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Alternativ 14 – Værdi | Value for alternative 14 for Custom Menu 4 (CM4Alt14Value)
|  |  | Alternativ 15 – Tekst | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Alternativ 15 – Værdi | Value for alternative 15 for Custom Menu 4 (CM4Alt15Value)
|  |  | Alternativ 16 – Tekst | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Alternativ 16 – Værdi | Value for alternative 16 for Custom Menu 4 (CM4Alt16Value)
|  |  | Alternativ 17 – Tekst | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Alternativ 17 – Værdi | Value for alternative 17 for Custom Menu 4 (CM4Alt17Value)
|  |  | Alternativ 18 – Tekst | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Alternativ 18 – Værdi | Value for alternative 18 for Custom Menu 4 (CM4Alt18Value)
|  |  | Alternativ 19 – Tekst | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Alternativ 19 – Værdi | Value for alternative 19 for Custom Menu 4 (CM4Alt19Value)
|  |  | Alternativ 20 – Tekst | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Alternativ 20 – Værdi | Value for alternative 20 for Custom Menu 4 (CM4Alt20Value)
|  |  | Alternativ 21 – Tekst | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Alternativ 21 – Værdi | Value for alternative 21 for Custom Menu 4 (CM4Alt21Value)
Brugerdefineret menu 5
|  |  | Titel | Title for Custom Menu 5 (CM5Title)
|  |  | Aktuel værdi | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Alternativ 1 – Tekst | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Alternativ 1 – Værdi | Value for alternative 1 for Custom Menu 5 (CM5Alt1Value)
|  |  | Alternativ 2 – Tekst | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Alternativ 2 – Værdi | Value for alternative 2 for Custom Menu 5 (CM5Alt2Value)
|  |  | Alternativ 3 – Tekst | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Alternativ 3 – Værdi | Value for alternative 3 for Custom Menu 5 (CM5Alt3Value)
|  |  | Alternativ 4 – Tekst | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Alternativ 4 – Værdi | Value for alternative 4 for Custom Menu 5 (CM5Alt4Value)
|  |  | Alternativ 5 – Tekst | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Alternativ 5 – Værdi | Value for alternative 5 for Custom Menu 5 (CM5Alt5Value)
|  |  | Alternativ 6 – Tekst | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Alternativ 6 – Værdi | Value for alternative 6 for Custom Menu 5 (CM5Alt6Value)
|  |  | Alternativ 7 – Tekst | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Alternativ 7 – Værdi | Value for alternative 7 for Custom Menu 5 (CM5Alt7Value)
|  |  | Alternativ 8 – Tekst | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Alternativ 8 – Værdi | Value for alternative 8 for Custom Menu 5 (CM5Alt8Value)
|  |  | Alternativ 9 – Tekst | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Alternativ 9 – Værdi | Value for alternative 9 for Custom Menu 5 (CM5Alt9Value)
|  |  | Alternativ 10 – Tekst | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Alternativ 10 – Værdi | Value for alternative 10 for Custom Menu 5 (CM5Alt10Value)
|  |  | Alternativ 11 – Tekst | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Alternativ 11 – Værdi | Value for alternative 11 for Custom Menu 5 (CM5Alt11Value)
|  |  | Alternativ 12 – Tekst | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Alternativ 12 – Værdi | Value for alternative 12 for Custom Menu 5 (CM5Alt12Value)
|  |  | Alternativ 13 – Tekst | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Alternativ 13 – Værdi | Value for alternative 13 for Custom Menu 5 (CM5Alt13Value)
|  |  | Alternativ 14 – Tekst | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Alternativ 14 – Værdi | Value for alternative 14 for Custom Menu 5 (CM5Alt14Value)
|  |  | Alternativ 15 – Tekst | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Alternativ 15 – Værdi | Value for alternative 15 for Custom Menu 5 (CM5Alt15Value)
|  |  | Alternativ 16 – Tekst | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Alternativ 16 – Værdi | Value for alternative 16 for Custom Menu 5 (CM5Alt16Value)
|  |  | Alternativ 17 – Tekst | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Alternativ 17 – Værdi | Value for alternative 17 for Custom Menu 5 (CM5Alt17Value)
|  |  | Alternativ 18 – Tekst | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Alternativ 18 – Værdi | Value for alternative 18 for Custom Menu 5 (CM5Alt18Value)
|  |  | Alternativ 19 – Tekst | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Alternativ 19 – Værdi | Value for alternative 19 for Custom Menu 5 (CM5Alt19Value)
|  |  | Alternativ 20 – Tekst | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Alternativ 20 – Værdi | Value for alternative 20 for Custom Menu 5 (CM5Alt20Value)
|  |  | Alternativ 21 – Tekst | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Alternativ 21 – Værdi | Value for alternative 21 for Custom Menu 5 (CM5Alt21Value)
Brugerdefineret menu 6
|  |  | Titel | Title for Custom Menu 6 (CM6Title)
|  |  | Aktuel værdi | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Alternativ 1 – Tekst | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Alternativ 1 – Værdi | Value for alternative 1 for Custom Menu 6 (CM6Alt1Value)
|  |  | Alternativ 2 – Tekst | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Alternativ 2 – Værdi | Value for alternative 2 for Custom Menu 6 (CM6Alt2Value)
|  |  | Alternativ 3 – Tekst | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Alternativ 3 – Værdi | Value for alternative 3 for Custom Menu 6 (CM6Alt3Value)
|  |  | Alternativ 4 – Tekst | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Alternativ 4 – Værdi | Value for alternative 4 for Custom Menu 6 (CM6Alt4Value)
|  |  | Alternativ 5 – Tekst | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Alternativ 5 – Værdi | Value for alternative 5 for Custom Menu 6 (CM6Alt5Value)
|  |  | Alternativ 6 – Tekst | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Alternativ 6 – Værdi | Value for alternative 6 for Custom Menu 6 (CM6Alt6Value)
|  |  | Alternativ 7 – Tekst | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Alternativ 7 – Værdi | Value for alternative 7 for Custom Menu 6 (CM6Alt7Value)
|  |  | Alternativ 8 – Tekst | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Alternativ 8 – Værdi | Value for alternative 8 for Custom Menu 6 (CM6Alt8Value)
|  |  | Alternativ 9 – Tekst | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Alternativ 9 – Værdi | Value for alternative 9 for Custom Menu 6 (CM6Alt9Value)
|  |  | Alternativ 10 – Tekst | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Alternativ 10 – Værdi | Value for alternative 10 for Custom Menu 6 (CM6Alt10Value)
|  |  | Alternativ 11 – Tekst | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Alternativ 11 – Værdi | Value for alternative 11 for Custom Menu 6 (CM6Alt11Value)
|  |  | Alternativ 12 – Tekst | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Alternativ 12 – Værdi | Value for alternative 12 for Custom Menu 6 (CM6Alt12Value)
|  |  | Alternativ 13 – Tekst | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Alternativ 13 – Værdi | Value for alternative 13 for Custom Menu 6 (CM6Alt13Value)
|  |  | Alternativ 14 – Tekst | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternativ 14 – Værdi | Value for alternative 14 for Custom Menu 6 (CM6Alt14Value)
|  |  | Alternativ 15 – Tekst | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Alternativ 15 – Værdi | Value for alternative 15 for Custom Menu 6 (CM6Alt15Value)
|  |  | Alternativ 16 – Tekst | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternativ 16 – Værdi | Value for alternative 16 for Custom Menu 6 (CM6Alt16Value)
|  |  | Alternativ 17 – Tekst | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Alternativ 17 – Værdi | Value for alternative 17 for Custom Menu 6 (CM6Alt17Value)
|  |  | Alternativ 18 – Tekst | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Alternativ 18 – Værdi | Value for alternative 18 for Custom Menu 6 (CM6Alt18Value)
|  |  | Alternativ 19 – Tekst | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Alternativ 19 – Værdi | Value for alternative 19 for Custom Menu 6 (CM6Alt19Value)
|  |  | Alternativ 20 – Tekst | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Alternativ 20 – Værdi | Value for alternative 20 for Custom Menu 6 (CM6Alt20Value)
|  |  | Alternativ 21 – Tekst | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Alternativ 21 – Værdi | Value for alternative 21 for Custom Menu 6 (CM6Alt21Value)
Brugerdefineret menu 7
|  |  | Titel | Title for Custom Menu 7 (CM7Title)
|  |  | Aktuel værdi | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Alternativ 1 – Tekst | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Alternativ 1 – Værdi | Value for alternative 1 for Custom Menu 7 (CM7Alt1Value)
|  |  | Alternativ 2 – Tekst | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Alternativ 2 – Værdi | Value for alternative 2 for Custom Menu 7 (CM7Alt2Value)
|  |  | Alternativ 3 – Tekst | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Alternativ 3 – Værdi | Value for alternative 3 for Custom Menu 7 (CM7Alt3Value)
|  |  | Alternativ 4 – Tekst | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Alternativ 4 – Værdi | Value for alternative 4 for Custom Menu 7 (CM7Alt4Value)
|  |  | Alternativ 5 – Tekst | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Alternativ 5 – Værdi | Value for alternative 5 for Custom Menu 7 (CM7Alt5Value)
|  |  | Alternativ 6 – Tekst | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Alternativ 6 – Værdi | Value for alternative 6 for Custom Menu 7 (CM7Alt6Value)
|  |  | Alternativ 7 – Tekst | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Alternativ 7 – Værdi | Value for alternative 7 for Custom Menu 7 (CM7Alt7Value)
|  |  | Alternativ 8 – Tekst | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Alternativ 8 – Værdi | Value for alternative 8 for Custom Menu 7 (CM7Alt8Value)
|  |  | Alternativ 9 – Tekst | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Alternativ 9 – Værdi | Value for alternative 9 for Custom Menu 7 (CM7Alt9Value)
|  |  | Alternativ 10 – Tekst | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Alternativ 10 – Værdi | Value for alternative 10 for Custom Menu 7 (CM7Alt10Value)
|  |  | Alternativ 11 – Tekst | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Alternativ 11 – Værdi | Value for alternative 11 for Custom Menu 7 (CM7Alt11Value)
|  |  | Alternativ 12 – Tekst | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Alternativ 12 – Værdi | Value for alternative 12 for Custom Menu 7 (CM7Alt12Value)
|  |  | Alternativ 13 – Tekst | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Alternativ 13 – Værdi | Value for alternative 13 for Custom Menu 7 (CM7Alt13Value)
|  |  | Alternativ 14 – Tekst | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Alternativ 14 – Værdi | Value for alternative 14 for Custom Menu 7 (CM7Alt14Value)
|  |  | Alternativ 15 – Tekst | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Alternativ 15 – Værdi | Value for alternative 15 for Custom Menu 7 (CM7Alt15Value)
|  |  | Alternativ 16 – Tekst | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Alternativ 16 – Værdi | Value for alternative 16 for Custom Menu 7 (CM7Alt16Value)
|  |  | Alternativ 17 – Tekst | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Alternativ 17 – Værdi | Value for alternative 17 for Custom Menu 7 (CM7Alt17Value)
|  |  | Alternativ 18 – Tekst | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Alternativ 18 – Værdi | Value for alternative 18 for Custom Menu 7 (CM7Alt18Value)
|  |  | Alternativ 19 – Tekst | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Alternativ 19 – Værdi | Value for alternative 19 for Custom Menu 7 (CM7Alt19Value)
|  |  | Alternativ 20 – Tekst | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Alternativ 20 – Værdi | Value for alternative 20 for Custom Menu 7 (CM7Alt20Value)
|  |  | Alternativ 21 – Tekst | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Alternativ 21 – Værdi | Value for alternative 21 for Custom Menu 7 (CM7Alt21Value)
Brugerdefineret menu 8
|  |  | Titel | Title for Custom Menu 8 (CM8Title)
|  |  | Aktuel værdi | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Alternativ 1 – Tekst | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Alternativ 1 – Værdi | Value for alternative 1 for Custom Menu 8 (CM8Alt1Value)
|  |  | Alternativ 2 – Tekst | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Alternativ 2 – Værdi | Value for alternative 2 for Custom Menu 8 (CM8Alt2Value)
|  |  | Alternativ 3 – Tekst | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Alternativ 3 – Værdi | Value for alternative 3 for Custom Menu 8 (CM8Alt3Value)
|  |  | Alternativ 4 – Tekst | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Alternativ 4 – Værdi | Value for alternative 4 for Custom Menu 8 (CM8Alt4Value)
|  |  | Alternativ 5 – Tekst | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Alternativ 5 – Værdi | Value for alternative 5 for Custom Menu 8 (CM8Alt5Value)
|  |  | Alternativ 6 – Tekst | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Alternativ 6 – Værdi | Value for alternative 6 for Custom Menu 8 (CM8Alt6Value)
|  |  | Alternativ 7 – Tekst | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Alternativ 7 – Værdi | Value for alternative 7 for Custom Menu 8 (CM8Alt7Value)
|  |  | Alternativ 8 – Tekst | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Alternativ 8 – Værdi | Value for alternative 8 for Custom Menu 8 (CM8Alt8Value)
|  |  | Alternativ 9 – Tekst | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Alternativ 9 – Værdi | Value for alternative 9 for Custom Menu 8 (CM8Alt9Value)
|  |  | Alternativ 10 – Tekst | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Alternativ 10 – Værdi | Value for alternative 10 for Custom Menu 8 (CM8Alt10Value)
|  |  | Alternativ 11 – Tekst | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Alternativ 11 – Værdi | Value for alternative 11 for Custom Menu 8 (CM8Alt11Value)
|  |  | Alternativ 12 – Tekst | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Alternativ 12 – Værdi | Value for alternative 12 for Custom Menu 8 (CM8Alt12Value)
|  |  | Alternativ 13 – Tekst | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Alternativ 13 – Værdi | Value for alternative 13 for Custom Menu 8 (CM8Alt13Value)
|  |  | Alternativ 14 – Tekst | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Alternativ 14 – Værdi | Value for alternative 14 for Custom Menu 8 (CM8Alt14Value)
|  |  | Alternativ 15 – Tekst | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Alternativ 15 – Værdi | Value for alternative 15 for Custom Menu 8 (CM8Alt15Value)
|  |  | Alternativ 16 – Tekst | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Alternativ 16 – Værdi | Value for alternative 16 for Custom Menu 8 (CM8Alt16Value)
|  |  | Alternativ 17 – Tekst | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Alternativ 17 – Værdi | Value for alternative 17 for Custom Menu 8 (CM8Alt17Value)
|  |  | Alternativ 18 – Tekst | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Alternativ 18 – Værdi | Value for alternative 18 for Custom Menu 8 (CM8Alt18Value)
|  |  | Alternativ 19 – Tekst | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Alternativ 19 – Værdi | Value for alternative 19 for Custom Menu 8 (CM8Alt19Value)
|  |  | Alternativ 20 – Tekst | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Alternativ 20 – Værdi | Value for alternative 20 for Custom Menu 8 (CM8Alt20Value)
|  |  | Alternativ 21 – Tekst | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Alternativ 21 – Værdi | Value for alternative 21 for Custom Menu 8 (CM8Alt21Value)
Aktuatorer
Tænd/sluk udgange
|  |  | Varme hysterese, rumtemperatur [ºC] | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Køling hysterese, rumtemperatur [ºC] | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysterese, ekstra zone temperatur [ºC] | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Ventilmotionering
|  |  | Test ventiler | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Varme interval [h] | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Varme 2 interval [h] | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Køle interval [h] | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Køle 2 interval [h] | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Change-over interval [h] | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | 6-vejsventil interval [h] | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Varme varighed [s] | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Varme 2 varighed [s] | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Køle varighed [s] | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Køle 2 varighed [s] | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Change-over varighed [s] | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | 6-vejsventil varighed [s] | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analoge indgange
Temperatur indgang
|  |  | Filtreringstid [s] | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperatur indgang 0-10 V
|  |  | Værdi ved 0 V [°C] | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Værdi ved 10 V [°C] | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2 indgang
|  |  | Værdi ved 0 V [ppm] | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Værdi ved 10 V [ppm] | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filtreringstid [s] | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Fugtighed indgang
|  |  | Værdi ved 0 V [%] | RH at 0 Volt input (RC_RH_0V)
|  |  | Værdi ved 10 V [%] | RH at 10 Volt input (RC_RH_10V)
|  |  | Filtreringstid [s] | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Flow indgang
|  |  | Værdi ved 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Værdi ved 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filtreringstid [s] | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC indgang
|  |  | Værdi ved 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Værdi ved 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filtreringstid [s] | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Sætpunkter
Rum sætpunkter
|  |  | Varme, occupied [°C] | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Køling, occupied [°C] | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Varme, standby [°C] | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Køling, standby [°C] | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Varme, unoccupied [°C] | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Køling, unoccupied [°C] | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Frost beskyttelse [°C] | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Sætpunkts justering
|  |  | Maks. op-justering [°C] | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Maks. ned-justering [°C] | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Sætpunkts justering [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Ekstra zone
|  |  | Ekstra zone sætpunkt [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2 sætpunkt [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Fugtighed
|  |  | Fugtighed sætpunkt [%] | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC sætpunkt | Setpoint for VOC control (RC_VOCSetpoint)
Kontroller indstillng
Rum
|  |  | P-bånd [°C] | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-time [s] | I-time for room PID controller (RC_RoomPIDItime)
Kaskade kontrol
|  |  | Styring aktiv | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Kaskade faktor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Maks. opvarmning temperatur [°C] | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min. opvarmning temperatur [°C] | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Maks. kølling temperatur [°C] | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min. køling temperatur [°C] | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Frost beskyttelses temperatur [°C] | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Ekstra zone
|  |  | P-bånd [°C] | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-time [s] | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-bånd [ppm] | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-time [s] | I-time for CO2 PID controller (RC_CO2PIDItime)
Fugtighed
|  |  | P-bånd [%] | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-time [s] | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-bånd | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-time [s] | I-time for VOC PID controller (RC_VOCPIDItime)
Alarm indstilling
Rumtemperatur alarm
|  |  | Høj grænse [°C] | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Lav grænse [°C] | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
CO2 niveaualarm
|  |  | Høj grænse [ppm] | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Indgangs justeringer
UI1
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_2_offset)
Rumtemperatur
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_5_offset)
Rum fugtighed
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_6_offset)
VOC føler
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_7_offset)
CO2 føler
|  |  | Grænser tilstand | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Forskydnings justering | Offset for input (IoAnaIn_8_offset)
Udgangs justeringer
UO1
|  |  | Min. værdi | Scale for output (IoAnaOut_1_min_in)
|  |  | Maks. værdi | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maksimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_max_out)
|  |  | Forskydning baseret på fuldt område [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Min. værdi | Scale for output (IoAnaOut_2_min_in)
|  |  | Maks. værdi | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maksimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_max_out)
|  |  | Forskydning baseret på fuldt område [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Min. værdi | Scale for output (IoAnaOut_3_min_in)
|  |  | Maks. værdi | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maksimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_max_out)
|  |  | Forskydning baseret på fuldt område [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Min. værdi | Scale for output (IoAnaOut_4_min_in)
|  |  | Maks. værdi | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maksimumsværdi [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_max_out)
|  |  | Forskydning baseret på fuldt område [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_4_offset)
Manuel/Auto
Fjern indgangsværdier
Rumtemperatur
|  |  | Fjern indstilling | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Indstillet værdi [°C] | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Rumtemperatur [°C] | Room temperature (RC_RoomTemp)
Tilluft temperatur
|  |  | Fjern indstilling | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Indstillet værdi [°C] | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Tilluft temperatur [°C] | Supply air temperature (RC_SupplyAirTemp)
Ekstra zone temperatur
|  |  | Fjern indstilling | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Indstillet værdi [°C] | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Ekstra zone temperatur [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
Change-over temperatur
|  |  | Fjern indstilling | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Indstillet værdi [°C] | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-over temperatur [°C] | Changeover temperature (RC_ChangeOverTemp)
Change-over temperatur
|  |  | Fjern indstilling | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Indstillet værdi [°C] | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-over temperatur [°C] | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2 niveau
|  |  | Fjern indstilling | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Indstillet værdi [ppm] | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2 niveau [ppm] | Room CO2 level (RC_CO2Level)
Rum fugtighed
|  |  | Fjern indstilling | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Indstillet værdi [%] | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Rum fugtighed [%] | Relative humidity (RC_Humidity)
Luft flow
|  |  | Fjern indstilling | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Indstillet værdi | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Luft flow | Air flow (RC_AirFlow)
VOC indeks
|  |  | Fjern indstilling | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Indstillet værdi | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC indeks | VOC index (RC_VOC)
Tilstedeværelses detektering
|  |  | Fjern indstilling | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Indstillet værdi | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Tilstedeværelses detektering | Presence indication (RC_Presence)
Åbent vindue
|  |  | Fjern indstilling | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Indstillet værdi | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Åbent vindue | Open window indication (RC_DIOpenWindow)
Kondensation
|  |  | Fjern indstilling | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Indstillet værdi | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Ekstern alarm (DI)
|  |  | Fjern indstilling | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Indstillet værdi | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | Ekstern alarm (DI) | Digital input alarm (RC_AlarmDI)
Change-over DI
|  |  | Fjern indstilling | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Indstillet værdi | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-over DI | Change-over digital input (RC_DIChangeOver)
Change-over VAV DI
|  |  | Fjern indstilling | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Indstillet værdi | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-over VAV DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Manuel/Auto
Controller tilstand
|  |  | Controller tilstand | Current state (RC_ControllerState)
|  |  | Fjern tilstand indstilling | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Nedlukning | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Tvungen ventilation | Set controller in Bypass state (RC_ControllerStateSetBypass)
Ventilator styre kilde
|  |  | Ventilator styre kilde | Fan speed setting (RC_FanSelect)
Varme udgang
|  |  | Tilstand | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Varme udgang [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Tilstand | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Varme udgang | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Varme 2 udgang
|  |  | Tilstand | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Varme 2 udgang [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Tilstand | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Varme 2 udgang | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Køling udgang
|  |  | Tilstand | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Køling udgang [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Tilstand | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Køling udgang | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Køling 2 udgang
|  |  | Tilstand | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Køling 2 udgang [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Tilstand | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Køling 2 udgang | Room control Cool2 output digital (RC_RoomCool2OutputDO)
VAV udgang
|  |  | Tilstand | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | VAV udgang [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
VAV 2 udgang
|  |  | Tilstand | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | VAV 2 udgang [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Change-over udgang
|  |  | Tilstand | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Change-over udgang [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Change-over VAV udgang
|  |  | Tilstand | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Change-over VAV udgang [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
6-vejsventil udgang
|  |  | Tilstand | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Tilstand | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Indstillet værdi [%] | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | 6-vejsventil udgang [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Ekstra zone udgang
|  |  | Tilstand | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Ekstra zone udgang | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC ventilator styring
|  |  | Tilstand | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Indstillet værdi [%] | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC ventilator styring [%] | Current EC fan speed (RC_ECFanSpeed)
CO2 kontrol udgang
|  |  | Tilstand | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Indstillet værdi [%] | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | CO2 kontrol udgang [%] | CO2 control analog out (RC_CO2ControlAO)
Fugtning kontrol udgang
|  |  | Tilstand | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Fugtning kontrol udgang [%] | Humidify analog out (RC_HumidifyOutputAO)
Affugtning kontrol udgang
|  |  | Tilstand | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Indstillet værdi [%] | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Affugtning kontrol udgang [%] | Dehumidify analog out (RC_DehumidifyOutputAO)
VOC kontrol udgang
|  |  | Tilstand | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Indstillet værdi [%] | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | VOC kontrol udgang [%] | VOC control analog out (RC_VOCControlAO)
Ekstra zone aktiv udgang
|  |  | Tilstand | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Ekstra zone aktiv udgang | Extra Zone active (RC_ExtraZoneActive)
Tvungen ventilation udgang
|  |  | Tilstand | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Tvungen ventilation udgang | Forced ventilation output (RC_ForcedVentDO)
Hardwarekontrol
UO1
|  |  | UO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Tilstand | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Indstillet værdi [0=0 %, 100=100 %] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Tilstand | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Indstillet værdi | Override value (IoDo_1_override)
UO2
|  |  | UO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Tilstand | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Indstillet værdi [0=0 %, 100=100 %] | Override value (IoAnaOut_2_override)
|  |  | UO2: | Value set for output (IoDo_2_value)
|  |  | Tilstand | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Indstillet værdi | Override value (IoDo_2_override)
AO1
|  |  | AO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Tilstand | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Indstillet værdi [0=0 %, 100=100 %] | Override value (IoAnaOut_3_override)
AO2
|  |  | AO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Tilstand | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Indstillet værdi [0=0 %, 100=100 %] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Tilstand | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Indstillet værdi | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Tilstand | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Indstillet værdi | Override value (IoAnaIn_2_override)
CO2-føler kalibrering
|  |  | Aktivér automatisk selv kalibrering | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Automatisk selvkalibrering baseline [ppm] [ppm] | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | Kør CO2 føler tvungen genkalibrering | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | Reference CO2 niveau for tvungen genkalibrering [ppm] [ppm] | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Sidste tvungne rekalibrerings resultat (-9999 = fejl) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | Nulstil CO2 føler | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Relæ udgang
|  |  | Relæ status | Value set for output (IoDo_3_value)
|  |  | Tilstand | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Indstillet værdi | Override value (IoDo_3_override)
PIR føler
|  |  | PIR føler | Filtered value from sensor (IoDiIn_4_value)
|  |  | Tilstand | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Indstillet værdi | Override value (IoDiIn_4_override)
Enhed
Enhed ID
Enhed ID
|  |  | Navn | (ControllerName)
|  |  | Beskrivelse | Controller description (ControllerDescription)
|  |  | Lokation | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Kommunikation
Port indstillinger
|  |  | Port 1 funktion | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Port 1 baudhastighed | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Port 1 paritet | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbus adresse | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | BACnet MSTP adresse | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | MSTP maks. masteradresse | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet enheds ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet enheds objektnavn | BACnet device object name (BACnetDeviceObjectName)
|  |  | Kodeord | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth funktion | Function for BLE button (BleButtonMode)
|  |  | Sluk efter [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | BLE transmissionseffekt | BLE TX power level (ble_power)
Kommunikations fejl
|  |  | Fejl handling | Offline function (RC_OfflineFunction)
|  |  | Timeout [s] | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Fallback tilstand | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Nulstil
Nulstil
|  |  | Genstart kontroller | Write to this register will trigger resets with different reset reasons (product_reset)
Ikke-flygtig lagring
Ikke-flygtig lagring
|  |  | Deaktiver ikke-flygtig lagring | Set to 1 to disable storage in non volatile memory (disable_nv_storage)

## de
RCX-2.1-1-01 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Übersicht
System
|  |  | Regler | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbus-Adresse | Active Modbus unit ID (ModbusUnitID)
|  |  | BACnet MSTP Adresse | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet Geräte-ID | BACnet device ID (BACnetDeviceID)
|  |  | Sammelalarm | Sum Alarm (RC_SumAlarm)
Raum
|  |  | Reglerstatus | Current state (RC_ControllerState)
|  |  | Betriebsmodus | Current controller mode (RC_ControllerMode)
|  |  | Raumtemperatur [°C] | Room temperature (RC_RoomTemp)
|  |  | Zulufttemperatur [°C] | Supply air temperature (RC_SupplyAirTemp)
|  |  | Raumsollwert [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Sollwertanpassung [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC-Ventilatordrehzahl [%] | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2-Gehalt [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Raumfeuchte [%] | Relative humidity (RC_Humidity)
|  |  | VOC-Index | VOC index (RC_VOC)
|  |  | Präsenzerkennung | Presence indication (RC_Presence)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Extrazone
|  |  | Extrazone Temperatur [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Extrazone Sollwert [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Extrazone aktiver Ausgang | Extra Zone active (RC_ExtraZoneActive)
Istwerte
Raumregler Sequenz
|  |  | Sequenz 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sequenz 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sequenz 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Istwerte
|  |  | Betriebsmodus | Current controller mode (RC_ControllerMode)
|  |  | Raumtemperatur [°C] | Room temperature (RC_RoomTemp)
|  |  | Raumsollwert [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Sollwertanpassung [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Heizanforderung [%] | Room PID heat output (RC_PIDHeatDemand)
|  |  | Kühlanforderung [%] | Room PID cool output (RC_PIDCoolDemand)
|  |  | Ausgang Heizen [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Ausgang Heizen 2 [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Ausgang Kühlen [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Ausgang Kühlen 2 [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Ausgang VVS [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | Ausgang VVS 2 [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-Over Temperatur | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-Over Status | Change-over status (RC_ChangeOverState)
|  |  | Ausgang Change-Over [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-Over VVS Temperatur | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-Over VVS Status | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Ausgang Change-Over VVS [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | Ausgang 6-Wege-Ventil [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2-Gehalt [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2-Sollwert [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Relaisausgang
|  |  | Status Relais | Value set for output (IoDo_3_value)
Eingänge/Ausgänge
Universaleingänge
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universalausgänge
|  |  | UO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analogausgänge
|  |  | AO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Interne Fühler
|  |  | Raumtemperatur [°C] | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2-Fühler [ppm] | Filtered value from sensor (IoAnaIn_8_value)
|  |  | Feuchtefühler [%] | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC-Sensor | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR-Sensor | Filtered value from sensor (IoDiIn_4_value)
Alarme
Alarme
|  |  | Sammelalarm | Sum Alarm (RC_SumAlarm)
|  |  | Fühlerfehler | Sensor error alarm (RC_AlarmSensorError)
|  |  | Hohe Raumtemperatur | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Niedrige Raumtemperatur | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | Hoher CO2-Gehalt | High CO2 alarm (RC_AlarmCO2High)
|  |  | Externer Alarm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Ausgang im Handbetrieb | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Fehlercode Temperaturfühler | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Fehlercode Feuchtefühler | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | Fehlercode VOC-Sensor | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | Fehlercode CO2-Fühler | Detailed fault description (IoAnaIn_8_errorFlags)
Info
Geräte-ID
|  |  | Seriennummer | (SerialNumberString)
|  |  | Name | (ControllerName)
|  |  | Beschreibung | Controller description (ControllerDescription)
|  |  | Standort | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Benutzerdefinierte Menüs
Benutzerdefiniertes Menü 1
|  |  | Titel | Title for Custom Menu 1 (CM1Title)
|  |  | Aktueller Wert | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Aktuelle Alternative | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Aktuelle Alternative | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Aktuelle Alternative | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Aktuelle Alternative | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Aktuelle Alternative | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Aktuelle Alternative | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Aktuelle Alternative | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Aktuelle Alternative | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Aktuelle Alternative | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Aktuelle Alternative | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Aktuelle Alternative | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Aktuelle Alternative | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Aktuelle Alternative | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Aktuelle Alternative | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Aktuelle Alternative | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Aktuelle Alternative | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Aktuelle Alternative | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Aktuelle Alternative | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Aktuelle Alternative | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Aktuelle Alternative | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Aktuelle Alternative | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Aktuelle Alternative Index | Current alternative for Custom Menu 1 (CM1CurrentAlt)
Benutzerdefiniertes Menü 2
|  |  | Titel | Title for Custom Menu 2 (CM2Title)
|  |  | Aktueller Wert | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Aktuelle Alternative | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Aktuelle Alternative | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Aktuelle Alternative | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Aktuelle Alternative | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Aktuelle Alternative | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Aktuelle Alternative | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Aktuelle Alternative | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Aktuelle Alternative | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Aktuelle Alternative | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Aktuelle Alternative | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Aktuelle Alternative | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Aktuelle Alternative | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Aktuelle Alternative | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Aktuelle Alternative | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Aktuelle Alternative | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Aktuelle Alternative | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Aktuelle Alternative | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Aktuelle Alternative | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Aktuelle Alternative | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Aktuelle Alternative | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Aktuelle Alternative | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Aktuelle Alternative Index | Current alternative for Custom Menu 2 (CM2CurrentAlt)
Benutzerdefiniertes Menü 3
|  |  | Titel | Title for Custom Menu 3 (CM3Title)
|  |  | Aktueller Wert | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Aktuelle Alternative | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Aktuelle Alternative | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Aktuelle Alternative | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Aktuelle Alternative | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Aktuelle Alternative | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Aktuelle Alternative | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Aktuelle Alternative | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Aktuelle Alternative | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Aktuelle Alternative | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Aktuelle Alternative | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Aktuelle Alternative | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Aktuelle Alternative | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Aktuelle Alternative | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Aktuelle Alternative | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Aktuelle Alternative | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Aktuelle Alternative | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Aktuelle Alternative | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Aktuelle Alternative | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Aktuelle Alternative | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Aktuelle Alternative | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Aktuelle Alternative | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Aktuelle Alternative Index | Current alternative for Custom Menu 3 (CM3CurrentAlt)
Benutzerdefiniertes Menü 4
|  |  | Titel | Title for Custom Menu 4 (CM4Title)
|  |  | Aktueller Wert | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Aktuelle Alternative | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Aktuelle Alternative | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Aktuelle Alternative | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Aktuelle Alternative | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Aktuelle Alternative | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Aktuelle Alternative | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Aktuelle Alternative | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Aktuelle Alternative | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Aktuelle Alternative | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Aktuelle Alternative | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Aktuelle Alternative | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Aktuelle Alternative | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Aktuelle Alternative | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Aktuelle Alternative | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Aktuelle Alternative | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Aktuelle Alternative | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Aktuelle Alternative | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Aktuelle Alternative | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Aktuelle Alternative | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Aktuelle Alternative | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Aktuelle Alternative | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Aktuelle Alternative Index | Current alternative for Custom Menu 4 (CM4CurrentAlt)
Benutzerdefiniertes Menü 5
|  |  | Titel | Title for Custom Menu 5 (CM5Title)
|  |  | Aktueller Wert | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Aktuelle Alternative | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Aktuelle Alternative | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Aktuelle Alternative | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Aktuelle Alternative | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Aktuelle Alternative | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Aktuelle Alternative | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Aktuelle Alternative | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Aktuelle Alternative | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Aktuelle Alternative | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Aktuelle Alternative | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Aktuelle Alternative | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Aktuelle Alternative | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Aktuelle Alternative | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Aktuelle Alternative | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Aktuelle Alternative | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Aktuelle Alternative | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Aktuelle Alternative | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Aktuelle Alternative | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Aktuelle Alternative | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Aktuelle Alternative | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Aktuelle Alternative | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Aktuelle Alternative Index | Current alternative for Custom Menu 5 (CM5CurrentAlt)
Benutzerdefiniertes Menü 6
|  |  | Titel | Title for Custom Menu 6 (CM6Title)
|  |  | Aktueller Wert | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Aktuelle Alternative | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Aktuelle Alternative | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Aktuelle Alternative | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Aktuelle Alternative | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Aktuelle Alternative | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Aktuelle Alternative | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Aktuelle Alternative | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Aktuelle Alternative | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Aktuelle Alternative | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Aktuelle Alternative | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Aktuelle Alternative | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Aktuelle Alternative | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Aktuelle Alternative | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Aktuelle Alternative | Text for alternative 14 for Custom Menu 6 (CM6Alt14Text)
|  |  | Aktuelle Alternative | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Aktuelle Alternative | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Aktuelle Alternative | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Aktuelle Alternative | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Aktuelle Alternative | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Aktuelle Alternative | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Aktuelle Alternative | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Aktuelle Alternative Index | Current alternative for Custom Menu 6 (CM6CurrentAlt)
Benutzerdefiniertes Menü 7
|  |  | Titel | Title for Custom Menu 7 (CM7Title)
|  |  | Aktueller Wert | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Aktuelle Alternative | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Aktuelle Alternative | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Aktuelle Alternative | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Aktuelle Alternative | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Aktuelle Alternative | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Aktuelle Alternative | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Aktuelle Alternative | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Aktuelle Alternative | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Aktuelle Alternative | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Aktuelle Alternative | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Aktuelle Alternative | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Aktuelle Alternative | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Aktuelle Alternative | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Aktuelle Alternative | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Aktuelle Alternative | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Aktuelle Alternative | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Aktuelle Alternative | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Aktuelle Alternative | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Aktuelle Alternative | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Aktuelle Alternative | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Aktuelle Alternative | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Aktuelle Alternative Index | Current alternative for Custom Menu 7 (CM7CurrentAlt)
Benutzerdefiniertes Menü 8
|  |  | Titel | Title for Custom Menu 8 (CM8Title)
|  |  | Aktueller Wert | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Aktuelle Alternative | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Aktuelle Alternative | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Aktuelle Alternative | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Aktuelle Alternative | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Aktuelle Alternative | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Aktuelle Alternative | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Aktuelle Alternative | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Aktuelle Alternative | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Aktuelle Alternative | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Aktuelle Alternative | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Aktuelle Alternative | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Aktuelle Alternative | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Aktuelle Alternative | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Aktuelle Alternative | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Aktuelle Alternative | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Aktuelle Alternative | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Aktuelle Alternative | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Aktuelle Alternative | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Aktuelle Alternative | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Aktuelle Alternative | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Aktuelle Alternative | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Aktuelle Alternative Index | Current alternative for Custom Menu 8 (CM8CurrentAlt)
Konfiguration
Reglerfunktionen
Raumregler Sequenz
|  |  | Sequenz 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sequenz 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sequenz 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Heizen
|  |  | Max.-Grenze [%] | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min.-Grenze [%] | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Ventilator Ausschaltverzögerung bei Elektroerhitzer | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Change-Over Status folgen | Heat1 included in change-over function (RC_Heat1InChangeOver)
Heizen 2
|  |  | Max.-Grenze [%] | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min.-Grenze [%] | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Ventilator Ausschaltverzögerung bei Elektroerhitzer | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Change-Over Status folgen | Heat2 included in change-over function (RC_Heat2InChangeOver)
Kühlen
|  |  | Max.-Grenze [%] | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min.-Grenze [%] | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Bei Zwangslüftung auf max. einstellen | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Ausgang ausschalten, wenn Ventilator aus | Turn off Cool1 output when the fan is off (RC_Cool1OffWhenFanIsOff)
|  |  | Change-Over Status folgen | Cool1 included in change-over function (RC_Cool1InChangeOver)
Kühlen 2
|  |  | Max.-Grenze [%] | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min.-Grenze [%] | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Bei Zwangslüftung auf max. einstellen | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Ausgang ausschalten, wenn Ventilator aus | Turn off Cool2 output when the fan is off (RC_Cool2OffWhenFanIsOff)
|  |  | Change-Over Status folgen | Cool2 included in change-over function (RC_Cool2InChangeOver)
VVS
|  |  | Max.-Grenze [%] | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min.-Grenze, Aus [%] | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min.-Grenze, Nicht belegt [%] | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min.-Grenze, Standby [%] | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min.-Grenze, Belegt [%] | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min.-Grenze, Zwangslüftung [%] | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Bei Zwangslüftung auf max. einstellen | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Max.-Grenze beim Heizen [%] | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Change-Over Status folgen | VAV1 included in change-over function (RC_VAV1InChangeOver)
|  |  | VVS starten, wenn vorherige Kühlsequenz erreicht [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | VVS starten, wenn vorherige Heizsequenz erreicht [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VVS 2
|  |  | Max.-Grenze [%] | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min.-Grenze, Aus [%] | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min.-Grenze, Nicht belegt [%] | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min.-Grenze, Standby [%] | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min.-Grenze, Belegt [%] | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min.-Grenze, Zwangslüftung [%] | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Bei Zwangslüftung auf max. einstellen | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Max.-Grenze beim Heizen [%] | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Change-Over Status folgen | VAV2 included in change-over function (RC_VAV2InChangeOver)
|  |  | VVS starten, wenn vorherige Kühlsequenz erreicht [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | VVS starten, wenn vorherige Heizsequenz erreicht [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VVS-Regelquelle
|  |  | Anforderung Kühlen | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2-Gehalt | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC-Index | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Feuchte | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-Over
|  |  | Max.-Grenze [%] | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min.-Grenze [%] | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Betriebsmodus | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-Over Temperatur [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Heizhysterese [°C] | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Kühlhysterese [°C] | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Verzögerungszeit Ventil [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-Over VVS
|  |  | Max.-Grenze [%] | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min.-Grenze, Aus [%] | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min.-Grenze, Nicht belegt [%] | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min.-Grenze, Standby [%] | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min.-Grenze, Belegt [%] | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min.-Grenze, Zwangslüftung [%] | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Bei Zwangslüftung auf max. einstellen | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Betriebsmodus | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-Over Temperatur [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Heizhysterese [°C] | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Kühlhysterese [°C] | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Verzögerungszeit Ventil [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
|  |  | VVS starten, wenn vorherige Kühlsequenz erreicht [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | VVS starten, wenn vorherige Heizsequenz erreicht [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
6-Wege Ventil
|  |  | Seq 1 voll offen [V] | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Seq 1 Start Öffnen [V] | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Seq 2 voll offen [V] | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Seq 2 Start Öffnen [V] | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Mittelpunkt [V] | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Mittelpunkt Hysterese [%] | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Sequenz-Reihenfolge | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Change-Over Status folgen | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Reglerstatus
|  |  | Voreingestellter Status | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Abschaltstatus | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Status Offenes Fenster | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Zeit im Status Zwangslüftung [min] | Bypass time (minutes) (RC_BypassTime)
Zwangslüftung
|  |  | Aktiviert wenn | Forced ventilation function (RC_ForcedVentMode)
|  |  | Startgrenze [%] | Forced ventilation start limit (RC_ForcedVentStartLimit)
Präsenzerkennung
|  |  | Status Präsenz | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Verzögerung aktiv [min] | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Verzögerung inaktiv [min] | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2 Aktivierung | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2-Gehalt [ppm] | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2 Hysterese [ppm] | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Internen PIR für Präsenz verwenden | Use internal PIR sensor for presence detection (RC_PIRPresence)
Extrazone
Extrazone
|  |  | Extrazone Funktion | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Deaktiviert unter Status | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Deaktivieren bei Abweichung Hauptzonenmodus von Funktion | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min.-Grenze [%] | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Max.-Grenze [%] | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Eingänge/Ausgänge
Universaleingänge
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universalausgänge
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | UO1 Pulsdauer thermischer Antrieb [s] | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | UO1 Stellsignal | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | UO2 Pulsdauer thermischer Antrieb [s] | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | UO2 Stellsignal | Unit converter (IoAnaOut_2_unit)
Analogausgänge
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO1 Stellsignal | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | AO2 Stellsignal | Unit converter (IoAnaOut_4_unit)
Ventilatorregelung
Ventilator Regelquelle
|  |  | Raumregler | Select fan control mode (RC_FanControlMode)
|  |  | CO2-Gehalt | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Feuchte | Fan is controlled by humidity output (RC_FanControlHumidity)
EC-Ventilatorregelung
|  |  | Ventilatorstufe bei keinem Bedarf | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Aus unterhalb Bedarf [%] | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysterese Reduzierung Ventilatorstufe [%] | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Start Ventilatorstufe [%] | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Max. Ventilatorstufe im Automatikbetrieb [%] | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Zwangslüftung Ventilatorstufe | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Zwangslüftung Ventilatorstufe [%] | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Stufe 1 Ausgang [%] | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Stufe 2 Ausgang [%] | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Stufe 3 Ausgang [%] | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Schimmelschutzfunktion | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Ventilator Kickstart
|  |  | Kickstart Dauer [s] | Fan kick start time (RC_FanKickStartTime)
Ventilator Ausschaltverzögerung
|  |  | Ausschaltverzögerungszeit [s] | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Minimale Ventilatorstufe | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Ventilator Boost
|  |  | Betriebsmodus | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Boost Dauer [s] | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-Band | Fan boost P band (RC_FanBoostPBand)
Display und Menüs
Display
|  |  | Startbildschirm | What to display during device startup (DisplayStartupMode)
|  |  | Anzeigemodus | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Sollwertmodus | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | CO2 auf den nächsten Wert runden | Min step for CO2 value (RC_CO2Step)
|  |  | Volle Helligkeit [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Dimmen Timeout, 0 = Immer voll [s] | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Helligkeit gedimmt [%] | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Aus Timeout, 0 = Nie aus [s] | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Display Ruhemodus
|  |  | Temperatur/Sollwert | Show temperature/setpoint in idle view (App_IdleViewTemperature)
|  |  | CO2-Gehalt | Show CO2 value in idle view (App_IdleViewCO2)
|  |  | Raumfeuchte | Show humidity in idle view (App_IdleViewHumidity)
|  |  | VOC-Index | Show VOC in idle view (App_IdleViewVOC)
|  |  | Reglerstatus | Show mode in idle view (App_IdleViewMode)
Menü
|  |  | Seite Sollwertanpassung | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Status Menüseite | Enable Mode menu page (App_EnableMenuMode)
|  |  | Change-Over Menüseite | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Ventilator Menüseite | Enable Fan menu page (App_EnableMenuFan)
|  |  | Zwangslüftung Menüseite | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Zwangslüftung Nachlauf | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Seite Temperatur/Sollwert | Enable Temperature menu page (App_EnableMenuTemp)
|  |  | Feuchte Menüseite | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | CO2 Menüseite | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | VOC Menüseite | Enable VOC menu page (App_EnableMenuVOC)
Anzeigereihenfolge
|  |  | Display Position 1 | Display position 1 (DisplayPosition1)
|  |  | Display Position 2 | Display position 2 (DisplayPosition2)
|  |  | Display Position 3 | Display position 3 (DisplayPosition3)
|  |  | Display Position 4 | Display position 4 (DisplayPosition4)
|  |  | Display Position 5 | Display position 5 (DisplayPosition5)
|  |  | Display Position 6 | Display position 6 (DisplayPosition6)
|  |  | Display Position 7 | Display position 7 (DisplayPosition7)
|  |  | Display Position 8 | Display position 8 (DisplayPosition8)
|  |  | Display Position 9 | Display position 9 (DisplayPosition9)
|  |  | Display Position 10 | Display position 10 (DisplayPosition10)
|  |  | Display Position 11 | Display position 11 (DisplayPosition11)
|  |  | Display Position 12 | Display position 12 (DisplayPosition12)
Benutzerdefinierte Menüoptionen
|  |  | Benutzerdefiniertes Menü 1 | Enable Custom Menu 1 (CM1Enabled)
|  |  | Benutzerdefiniertes Menü 2 | Enable Custom Menu 2 (CM2Enabled)
|  |  | Benutzerdefiniertes Menü 3 | Enable Custom Menu 3 (CM3Enabled)
|  |  | Benutzerdefiniertes Menü 4 | Enable Custom Menu 4 (CM4Enabled)
|  |  | Benutzerdefiniertes Menü 5 | Enable Custom Menu 5 (CM5Enabled)
|  |  | Benutzerdefiniertes Menü 6 | Enable Custom Menu 6 (CM6Enabled)
|  |  | Benutzerdefiniertes Menü 7 | Enable Custom Menu 7 (CM7Enabled)
|  |  | Benutzerdefiniertes Menü 8 | Enable Custom Menu 8 (CM8Enabled)
Menüoptionen Status
|  |  | Menü Titeltext | Mode menu title (App_ModeMenuTitle)
|  |  | Status Aus aktivieren | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Status Nicht belegt aktivieren | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Status Standby aktivieren | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Status Belegt aktivieren | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Status Zwangslüftung aktivieren | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Status Aus Text | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Status Nicht belegt Text | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Status Standby Text | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Status Belegt Text | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Status Zwangslüftung Text | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Status Auto Text | Mode menu Auto state text (App_ModeMenuAutoText)
Menüoptionen Change-Over
|  |  | Menü Titeltext | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | Modus Heizen aktivieren | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | Modus Kühlen aktivieren | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | Modus Auto aktivieren | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | Modus Heizen Text | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | Modus Kühlen Text | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | Modus Auto Text | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
LED-Anzeige
|  |  | Helligkeit [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 LED-Anzeige | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Gelbe LED CO2-Gehalt [ppm] | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Rote LED CO2-Gehalt [ppm] | CO2 level for red led (RC_CO2LevelRed)
Benutzerdefinierte Texte
|  |  | Anzeigemodus | When to show the custom text (rt_text_visability)
|  |  | Anzeigemodus | Single or dual row text in display (rt_text_mode)
|  |  | Scrollmodus | Scroll mode (rt_text_display_scroll_mode)
|  |  | Schriftart | What font to use for the display text (rt_text_font)
|  |  | Scrollverzögerung [ms] | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Benutzerdefinierter Text Timer-Wert [s] | Time to show the custom text (rt_text_timeleft)
|  |  | Benutzerdefinierter Text Zeile 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Benutzerdefinierter Text Zeile 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Benutzerdefinierter Text 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Benutzerdefinierter Text 2 | String to show on row 2 in the display (rt_text_row_2)
Benutzerdefinierte Menüs
Benutzerdefiniertes Menü 1
|  |  | Titel | Title for Custom Menu 1 (CM1Title)
|  |  | Aktueller Wert | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Alternative 1 – Text | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Alternative 1 – Wert | Value for alternative 1 for Custom Menu 1 (CM1Alt1Value)
|  |  | Alternative 2 – Text | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Alternative 2 – Wert | Value for alternative 2 for Custom Menu 1 (CM1Alt2Value)
|  |  | Alternative 3 – Text | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Alternative 3 – Wert | Value for alternative 3 for Custom Menu 1 (CM1Alt3Value)
|  |  | Alternative 4 – Text | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Alternative 4 – Wert | Value for alternative 4 for Custom Menu 1 (CM1Alt4Value)
|  |  | Alternative 5 – Text | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Alternative 5 – Wert | Value for alternative 5 for Custom Menu 1 (CM1Alt5Value)
|  |  | Alternative 6 – Text | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Alternative 6 – Wert | Value for alternative 6 for Custom Menu 1 (CM1Alt6Value)
|  |  | Alternative 7 – Text | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Alternative 7 – Wert | Value for alternative 7 for Custom Menu 1 (CM1Alt7Value)
|  |  | Alternative 8 – Text | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Alternative 8 – Wert | Value for alternative 8 for Custom Menu 1 (CM1Alt8Value)
|  |  | Alternative 9 – Text | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Alternative 9 – Wert | Value for alternative 9 for Custom Menu 1 (CM1Alt9Value)
|  |  | Alternative 10 – Text | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Alternative 10 – Wert | Value for alternative 10 for Custom Menu 1 (CM1Alt10Value)
|  |  | Alternative 11 – Text | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Alternative 11 – Wert | Value for alternative 11 for Custom Menu 1 (CM1Alt11Value)
|  |  | Alternative 12 – Text | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Alternative 12 – Wert | Value for alternative 12 for Custom Menu 1 (CM1Alt12Value)
|  |  | Alternative 13 – Text | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Alternative 13 – Wert | Value for alternative 13 for Custom Menu 1 (CM1Alt13Value)
|  |  | Alternative 14 – Text | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Alternative 14 – Wert | Value for alternative 14 for Custom Menu 1 (CM1Alt14Value)
|  |  | Alternative 15 – Text | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Alternative 15 – Wert | Value for alternative 15 for Custom Menu 1 (CM1Alt15Value)
|  |  | Alternative 16 – Text | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Alternative 16 – Wert | Value for alternative 16 for Custom Menu 1 (CM1Alt16Value)
|  |  | Alternative 17 – Text | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Alternative 17 – Wert | Value for alternative 17 for Custom Menu 1 (CM1Alt17Value)
|  |  | Alternative 18 – Text | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Alternative 18 – Wert | Value for alternative 18 for Custom Menu 1 (CM1Alt18Value)
|  |  | Alternative 19 – Text | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Alternative 19 – Wert | Value for alternative 19 for Custom Menu 1 (CM1Alt19Value)
|  |  | Alternative 20 – Text | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Alternative 20 – Wert | Value for alternative 20 for Custom Menu 1 (CM1Alt20Value)
|  |  | Alternative 21 – Text | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Alternative 21 – Wert | Value for alternative 21 for Custom Menu 1 (CM1Alt21Value)
Benutzerdefiniertes Menü 2
|  |  | Titel | Title for Custom Menu 2 (CM2Title)
|  |  | Aktueller Wert | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Alternative 1 – Text | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Alternative 1 – Wert | Value for alternative 1 for Custom Menu 2 (CM2Alt1Value)
|  |  | Alternative 2 – Text | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Alternative 2 – Wert | Value for alternative 2 for Custom Menu 2 (CM2Alt2Value)
|  |  | Alternative 3 – Text | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Alternative 3 – Wert | Value for alternative 3 for Custom Menu 2 (CM2Alt3Value)
|  |  | Alternative 4 – Text | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Alternative 4 – Wert | Value for alternative 4 for Custom Menu 2 (CM2Alt4Value)
|  |  | Alternative 5 – Text | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Alternative 5 – Wert | Value for alternative 5 for Custom Menu 2 (CM2Alt5Value)
|  |  | Alternative 6 – Text | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Alternative 6 – Wert | Value for alternative 6 for Custom Menu 2 (CM2Alt6Value)
|  |  | Alternative 7 – Text | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Alternative 7 – Wert | Value for alternative 7 for Custom Menu 2 (CM2Alt7Value)
|  |  | Alternative 8 – Text | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Alternative 8 – Wert | Value for alternative 8 for Custom Menu 2 (CM2Alt8Value)
|  |  | Alternative 9 – Text | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Alternative 9 – Wert | Value for alternative 9 for Custom Menu 2 (CM2Alt9Value)
|  |  | Alternative 10 – Text | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Alternative 10 – Wert | Value for alternative 10 for Custom Menu 2 (CM2Alt10Value)
|  |  | Alternative 11 – Text | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Alternative 11 – Wert | Value for alternative 11 for Custom Menu 2 (CM2Alt11Value)
|  |  | Alternative 12 – Text | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Alternative 12 – Wert | Value for alternative 12 for Custom Menu 2 (CM2Alt12Value)
|  |  | Alternative 13 – Text | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Alternative 13 – Wert | Value for alternative 13 for Custom Menu 2 (CM2Alt13Value)
|  |  | Alternative 14 – Text | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Alternative 14 – Wert | Value for alternative 14 for Custom Menu 2 (CM2Alt14Value)
|  |  | Alternative 15 – Text | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Alternative 15 – Wert | Value for alternative 15 for Custom Menu 2 (CM2Alt15Value)
|  |  | Alternative 16 – Text | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Alternative 16 – Wert | Value for alternative 16 for Custom Menu 2 (CM2Alt16Value)
|  |  | Alternative 17 – Text | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Alternative 17 – Wert | Value for alternative 17 for Custom Menu 2 (CM2Alt17Value)
|  |  | Alternative 18 – Text | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Alternative 18 – Wert | Value for alternative 18 for Custom Menu 2 (CM2Alt18Value)
|  |  | Alternative 19 – Text | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Alternative 19 – Wert | Value for alternative 19 for Custom Menu 2 (CM2Alt19Value)
|  |  | Alternative 20 – Text | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Alternative 20 – Wert | Value for alternative 20 for Custom Menu 2 (CM2Alt20Value)
|  |  | Alternative 21 – Text | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Alternative 21 – Wert | Value for alternative 21 for Custom Menu 2 (CM2Alt21Value)
Benutzerdefiniertes Menü 3
|  |  | Titel | Title for Custom Menu 3 (CM3Title)
|  |  | Aktueller Wert | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Alternative 1 – Text | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Alternative 1 – Wert | Value for alternative 1 for Custom Menu 3 (CM3Alt1Value)
|  |  | Alternative 2 – Text | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Alternative 2 – Wert | Value for alternative 2 for Custom Menu 3 (CM3Alt2Value)
|  |  | Alternative 3 – Text | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Alternative 3 – Wert | Value for alternative 3 for Custom Menu 3 (CM3Alt3Value)
|  |  | Alternative 4 – Text | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Alternative 4 – Wert | Value for alternative 4 for Custom Menu 3 (CM3Alt4Value)
|  |  | Alternative 5 – Text | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Alternative 5 – Wert | Value for alternative 5 for Custom Menu 3 (CM3Alt5Value)
|  |  | Alternative 6 – Text | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Alternative 6 – Wert | Value for alternative 6 for Custom Menu 3 (CM3Alt6Value)
|  |  | Alternative 7 – Text | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Alternative 7 – Wert | Value for alternative 7 for Custom Menu 3 (CM3Alt7Value)
|  |  | Alternative 8 – Text | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Alternative 8 – Wert | Value for alternative 8 for Custom Menu 3 (CM3Alt8Value)
|  |  | Alternative 9 – Text | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Alternative 9 – Wert | Value for alternative 9 for Custom Menu 3 (CM3Alt9Value)
|  |  | Alternative 10 – Text | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Alternative 10 – Wert | Value for alternative 10 for Custom Menu 3 (CM3Alt10Value)
|  |  | Alternative 11 – Text | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Alternative 11 – Wert | Value for alternative 11 for Custom Menu 3 (CM3Alt11Value)
|  |  | Alternative 12 – Text | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Alternative 12 – Wert | Value for alternative 12 for Custom Menu 3 (CM3Alt12Value)
|  |  | Alternative 13 – Text | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Alternative 13 – Wert | Value for alternative 13 for Custom Menu 3 (CM3Alt13Value)
|  |  | Alternative 14 – Text | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Alternative 14 – Wert | Value for alternative 14 for Custom Menu 3 (CM3Alt14Value)
|  |  | Alternative 15 – Text | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Alternative 15 – Wert | Value for alternative 15 for Custom Menu 3 (CM3Alt15Value)
|  |  | Alternative 16 – Text | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Alternative 16 – Wert | Value for alternative 16 for Custom Menu 3 (CM3Alt16Value)
|  |  | Alternative 17 – Text | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Alternative 17 – Wert | Value for alternative 17 for Custom Menu 3 (CM3Alt17Value)
|  |  | Alternative 18 – Text | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Alternative 18 – Wert | Value for alternative 18 for Custom Menu 3 (CM3Alt18Value)
|  |  | Alternative 19 – Text | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Alternative 19 – Wert | Value for alternative 19 for Custom Menu 3 (CM3Alt19Value)
|  |  | Alternative 20 – Text | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Alternative 20 – Wert | Value for alternative 20 for Custom Menu 3 (CM3Alt20Value)
|  |  | Alternative 21 – Text | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Alternative 21 – Wert | Value for alternative 21 for Custom Menu 3 (CM3Alt21Value)
Benutzerdefiniertes Menü 4
|  |  | Titel | Title for Custom Menu 4 (CM4Title)
|  |  | Aktueller Wert | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Alternative 1 – Text | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Alternative 1 – Wert | Value for alternative 1 for Custom Menu 4 (CM4Alt1Value)
|  |  | Alternative 2 – Text | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Alternative 2 – Wert | Value for alternative 2 for Custom Menu 4 (CM4Alt2Value)
|  |  | Alternative 3 – Text | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Alternative 3 – Wert | Value for alternative 3 for Custom Menu 4 (CM4Alt3Value)
|  |  | Alternative 4 – Text | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Alternative 4 – Wert | Value for alternative 4 for Custom Menu 4 (CM4Alt4Value)
|  |  | Alternative 5 – Text | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Alternative 5 – Wert | Value for alternative 5 for Custom Menu 4 (CM4Alt5Value)
|  |  | Alternative 6 – Text | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Alternative 6 – Wert | Value for alternative 6 for Custom Menu 4 (CM4Alt6Value)
|  |  | Alternative 7 – Text | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Alternative 7 – Wert | Value for alternative 7 for Custom Menu 4 (CM4Alt7Value)
|  |  | Alternative 8 – Text | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Alternative 8 – Wert | Value for alternative 8 for Custom Menu 4 (CM4Alt8Value)
|  |  | Alternative 9 – Text | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Alternative 9 – Wert | Value for alternative 9 for Custom Menu 4 (CM4Alt9Value)
|  |  | Alternative 10 – Text | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Alternative 10 – Wert | Value for alternative 10 for Custom Menu 4 (CM4Alt10Value)
|  |  | Alternative 11 – Text | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Alternative 11 – Wert | Value for alternative 11 for Custom Menu 4 (CM4Alt11Value)
|  |  | Alternative 12 – Text | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Alternative 12 – Wert | Value for alternative 12 for Custom Menu 4 (CM4Alt12Value)
|  |  | Alternative 13 – Text | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Alternative 13 – Wert | Value for alternative 13 for Custom Menu 4 (CM4Alt13Value)
|  |  | Alternative 14 – Text | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Alternative 14 – Wert | Value for alternative 14 for Custom Menu 4 (CM4Alt14Value)
|  |  | Alternative 15 – Text | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Alternative 15 – Wert | Value for alternative 15 for Custom Menu 4 (CM4Alt15Value)
|  |  | Alternative 16 – Text | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Alternative 16 – Wert | Value for alternative 16 for Custom Menu 4 (CM4Alt16Value)
|  |  | Alternative 17 – Text | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Alternative 17 – Wert | Value for alternative 17 for Custom Menu 4 (CM4Alt17Value)
|  |  | Alternative 18 – Text | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Alternative 18 – Wert | Value for alternative 18 for Custom Menu 4 (CM4Alt18Value)
|  |  | Alternative 19 – Text | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Alternative 19 – Wert | Value for alternative 19 for Custom Menu 4 (CM4Alt19Value)
|  |  | Alternative 20 – Text | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Alternative 20 – Wert | Value for alternative 20 for Custom Menu 4 (CM4Alt20Value)
|  |  | Alternative 21 – Text | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Alternative 21 – Wert | Value for alternative 21 for Custom Menu 4 (CM4Alt21Value)
Benutzerdefiniertes Menü 5
|  |  | Titel | Title for Custom Menu 5 (CM5Title)
|  |  | Aktueller Wert | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Alternative 1 – Text | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Alternative 1 – Wert | Value for alternative 1 for Custom Menu 5 (CM5Alt1Value)
|  |  | Alternative 2 – Text | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Alternative 2 – Wert | Value for alternative 2 for Custom Menu 5 (CM5Alt2Value)
|  |  | Alternative 3 – Text | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Alternative 3 – Wert | Value for alternative 3 for Custom Menu 5 (CM5Alt3Value)
|  |  | Alternative 4 – Text | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Alternative 4 – Wert | Value for alternative 4 for Custom Menu 5 (CM5Alt4Value)
|  |  | Alternative 5 – Text | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Alternative 5 – Wert | Value for alternative 5 for Custom Menu 5 (CM5Alt5Value)
|  |  | Alternative 6 – Text | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Alternative 6 – Wert | Value for alternative 6 for Custom Menu 5 (CM5Alt6Value)
|  |  | Alternative 7 – Text | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Alternative 7 – Wert | Value for alternative 7 for Custom Menu 5 (CM5Alt7Value)
|  |  | Alternative 8 – Text | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Alternative 8 – Wert | Value for alternative 8 for Custom Menu 5 (CM5Alt8Value)
|  |  | Alternative 9 – Text | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Alternative 9 – Wert | Value for alternative 9 for Custom Menu 5 (CM5Alt9Value)
|  |  | Alternative 10 – Text | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Alternative 10 – Wert | Value for alternative 10 for Custom Menu 5 (CM5Alt10Value)
|  |  | Alternative 11 – Text | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Alternative 11 – Wert | Value for alternative 11 for Custom Menu 5 (CM5Alt11Value)
|  |  | Alternative 12 – Text | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Alternative 12 – Wert | Value for alternative 12 for Custom Menu 5 (CM5Alt12Value)
|  |  | Alternative 13 – Text | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Alternative 13 – Wert | Value for alternative 13 for Custom Menu 5 (CM5Alt13Value)
|  |  | Alternative 14 – Text | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Alternative 14 – Wert | Value for alternative 14 for Custom Menu 5 (CM5Alt14Value)
|  |  | Alternative 15 – Text | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Alternative 15 – Wert | Value for alternative 15 for Custom Menu 5 (CM5Alt15Value)
|  |  | Alternative 16 – Text | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Alternative 16 – Wert | Value for alternative 16 for Custom Menu 5 (CM5Alt16Value)
|  |  | Alternative 17 – Text | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Alternative 17 – Wert | Value for alternative 17 for Custom Menu 5 (CM5Alt17Value)
|  |  | Alternative 18 – Text | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Alternative 18 – Wert | Value for alternative 18 for Custom Menu 5 (CM5Alt18Value)
|  |  | Alternative 19 – Text | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Alternative 19 – Wert | Value for alternative 19 for Custom Menu 5 (CM5Alt19Value)
|  |  | Alternative 20 – Text | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Alternative 20 – Wert | Value for alternative 20 for Custom Menu 5 (CM5Alt20Value)
|  |  | Alternative 21 – Text | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Alternative 21 – Wert | Value for alternative 21 for Custom Menu 5 (CM5Alt21Value)
Benutzerdefiniertes Menü 6
|  |  | Titel | Title for Custom Menu 6 (CM6Title)
|  |  | Aktueller Wert | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Alternative 1 – Text | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Alternative 1 – Wert | Value for alternative 1 for Custom Menu 6 (CM6Alt1Value)
|  |  | Alternative 2 – Text | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Alternative 2 – Wert | Value for alternative 2 for Custom Menu 6 (CM6Alt2Value)
|  |  | Alternative 3 – Text | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Alternative 3 – Wert | Value for alternative 3 for Custom Menu 6 (CM6Alt3Value)
|  |  | Alternative 4 – Text | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Alternative 4 – Wert | Value for alternative 4 for Custom Menu 6 (CM6Alt4Value)
|  |  | Alternative 5 – Text | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Alternative 5 – Wert | Value for alternative 5 for Custom Menu 6 (CM6Alt5Value)
|  |  | Alternative 6 – Text | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Alternative 6 – Wert | Value for alternative 6 for Custom Menu 6 (CM6Alt6Value)
|  |  | Alternative 7 – Text | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Alternative 7 – Wert | Value for alternative 7 for Custom Menu 6 (CM6Alt7Value)
|  |  | Alternative 8 – Text | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Alternative 8 – Wert | Value for alternative 8 for Custom Menu 6 (CM6Alt8Value)
|  |  | Alternative 9 – Text | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Alternative 9 – Wert | Value for alternative 9 for Custom Menu 6 (CM6Alt9Value)
|  |  | Alternative 10 – Text | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Alternative 10 – Wert | Value for alternative 10 for Custom Menu 6 (CM6Alt10Value)
|  |  | Alternative 11 – Text | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Alternative 11 – Wert | Value for alternative 11 for Custom Menu 6 (CM6Alt11Value)
|  |  | Alternative 12 – Text | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Alternative 12 – Wert | Value for alternative 12 for Custom Menu 6 (CM6Alt12Value)
|  |  | Alternative 13 – Text | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Alternative 13 – Wert | Value for alternative 13 for Custom Menu 6 (CM6Alt13Value)
|  |  | Alternative 14 – Text | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternative 14 – Wert | Value for alternative 14 for Custom Menu 6 (CM6Alt14Value)
|  |  | Alternative 15 – Text | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Alternative 15 – Wert | Value for alternative 15 for Custom Menu 6 (CM6Alt15Value)
|  |  | Alternative 16 – Text | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternative 16 – Wert | Value for alternative 16 for Custom Menu 6 (CM6Alt16Value)
|  |  | Alternative 17 – Text | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Alternative 17 – Wert | Value for alternative 17 for Custom Menu 6 (CM6Alt17Value)
|  |  | Alternative 18 – Text | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Alternative 18 – Wert | Value for alternative 18 for Custom Menu 6 (CM6Alt18Value)
|  |  | Alternative 19 – Text | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Alternative 19 – Wert | Value for alternative 19 for Custom Menu 6 (CM6Alt19Value)
|  |  | Alternative 20 – Text | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Alternative 20 – Wert | Value for alternative 20 for Custom Menu 6 (CM6Alt20Value)
|  |  | Alternative 21 – Text | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Alternative 21 – Wert | Value for alternative 21 for Custom Menu 6 (CM6Alt21Value)
Benutzerdefiniertes Menü 7
|  |  | Titel | Title for Custom Menu 7 (CM7Title)
|  |  | Aktueller Wert | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Alternative 1 – Text | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Alternative 1 – Wert | Value for alternative 1 for Custom Menu 7 (CM7Alt1Value)
|  |  | Alternative 2 – Text | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Alternative 2 – Wert | Value for alternative 2 for Custom Menu 7 (CM7Alt2Value)
|  |  | Alternative 3 – Text | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Alternative 3 – Wert | Value for alternative 3 for Custom Menu 7 (CM7Alt3Value)
|  |  | Alternative 4 – Text | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Alternative 4 – Wert | Value for alternative 4 for Custom Menu 7 (CM7Alt4Value)
|  |  | Alternative 5 – Text | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Alternative 5 – Wert | Value for alternative 5 for Custom Menu 7 (CM7Alt5Value)
|  |  | Alternative 6 – Text | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Alternative 6 – Wert | Value for alternative 6 for Custom Menu 7 (CM7Alt6Value)
|  |  | Alternative 7 – Text | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Alternative 7 – Wert | Value for alternative 7 for Custom Menu 7 (CM7Alt7Value)
|  |  | Alternative 8 – Text | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Alternative 8 – Wert | Value for alternative 8 for Custom Menu 7 (CM7Alt8Value)
|  |  | Alternative 9 – Text | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Alternative 9 – Wert | Value for alternative 9 for Custom Menu 7 (CM7Alt9Value)
|  |  | Alternative 10 – Text | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Alternative 10 – Wert | Value for alternative 10 for Custom Menu 7 (CM7Alt10Value)
|  |  | Alternative 11 – Text | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Alternative 11 – Wert | Value for alternative 11 for Custom Menu 7 (CM7Alt11Value)
|  |  | Alternative 12 – Text | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Alternative 12 – Wert | Value for alternative 12 for Custom Menu 7 (CM7Alt12Value)
|  |  | Alternative 13 – Text | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Alternative 13 – Wert | Value for alternative 13 for Custom Menu 7 (CM7Alt13Value)
|  |  | Alternative 14 – Text | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Alternative 14 – Wert | Value for alternative 14 for Custom Menu 7 (CM7Alt14Value)
|  |  | Alternative 15 – Text | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Alternative 15 – Wert | Value for alternative 15 for Custom Menu 7 (CM7Alt15Value)
|  |  | Alternative 16 – Text | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Alternative 16 – Wert | Value for alternative 16 for Custom Menu 7 (CM7Alt16Value)
|  |  | Alternative 17 – Text | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Alternative 17 – Wert | Value for alternative 17 for Custom Menu 7 (CM7Alt17Value)
|  |  | Alternative 18 – Text | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Alternative 18 – Wert | Value for alternative 18 for Custom Menu 7 (CM7Alt18Value)
|  |  | Alternative 19 – Text | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Alternative 19 – Wert | Value for alternative 19 for Custom Menu 7 (CM7Alt19Value)
|  |  | Alternative 20 – Text | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Alternative 20 – Wert | Value for alternative 20 for Custom Menu 7 (CM7Alt20Value)
|  |  | Alternative 21 – Text | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Alternative 21 – Wert | Value for alternative 21 for Custom Menu 7 (CM7Alt21Value)
Benutzerdefiniertes Menü 8
|  |  | Titel | Title for Custom Menu 8 (CM8Title)
|  |  | Aktueller Wert | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Alternative 1 – Text | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Alternative 1 – Wert | Value for alternative 1 for Custom Menu 8 (CM8Alt1Value)
|  |  | Alternative 2 – Text | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Alternative 2 – Wert | Value for alternative 2 for Custom Menu 8 (CM8Alt2Value)
|  |  | Alternative 3 – Text | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Alternative 3 – Wert | Value for alternative 3 for Custom Menu 8 (CM8Alt3Value)
|  |  | Alternative 4 – Text | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Alternative 4 – Wert | Value for alternative 4 for Custom Menu 8 (CM8Alt4Value)
|  |  | Alternative 5 – Text | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Alternative 5 – Wert | Value for alternative 5 for Custom Menu 8 (CM8Alt5Value)
|  |  | Alternative 6 – Text | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Alternative 6 – Wert | Value for alternative 6 for Custom Menu 8 (CM8Alt6Value)
|  |  | Alternative 7 – Text | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Alternative 7 – Wert | Value for alternative 7 for Custom Menu 8 (CM8Alt7Value)
|  |  | Alternative 8 – Text | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Alternative 8 – Wert | Value for alternative 8 for Custom Menu 8 (CM8Alt8Value)
|  |  | Alternative 9 – Text | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Alternative 9 – Wert | Value for alternative 9 for Custom Menu 8 (CM8Alt9Value)
|  |  | Alternative 10 – Text | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Alternative 10 – Wert | Value for alternative 10 for Custom Menu 8 (CM8Alt10Value)
|  |  | Alternative 11 – Text | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Alternative 11 – Wert | Value for alternative 11 for Custom Menu 8 (CM8Alt11Value)
|  |  | Alternative 12 – Text | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Alternative 12 – Wert | Value for alternative 12 for Custom Menu 8 (CM8Alt12Value)
|  |  | Alternative 13 – Text | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Alternative 13 – Wert | Value for alternative 13 for Custom Menu 8 (CM8Alt13Value)
|  |  | Alternative 14 – Text | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Alternative 14 – Wert | Value for alternative 14 for Custom Menu 8 (CM8Alt14Value)
|  |  | Alternative 15 – Text | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Alternative 15 – Wert | Value for alternative 15 for Custom Menu 8 (CM8Alt15Value)
|  |  | Alternative 16 – Text | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Alternative 16 – Wert | Value for alternative 16 for Custom Menu 8 (CM8Alt16Value)
|  |  | Alternative 17 – Text | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Alternative 17 – Wert | Value for alternative 17 for Custom Menu 8 (CM8Alt17Value)
|  |  | Alternative 18 – Text | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Alternative 18 – Wert | Value for alternative 18 for Custom Menu 8 (CM8Alt18Value)
|  |  | Alternative 19 – Text | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Alternative 19 – Wert | Value for alternative 19 for Custom Menu 8 (CM8Alt19Value)
|  |  | Alternative 20 – Text | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Alternative 20 – Wert | Value for alternative 20 for Custom Menu 8 (CM8Alt20Value)
|  |  | Alternative 21 – Text | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Alternative 21 – Wert | Value for alternative 21 for Custom Menu 8 (CM8Alt21Value)
Stellantriebe
Ein/Aus-Ausgänge
|  |  | Heizhysterese, Raumtemperatur [ºC] | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Kühlhysterese, Raumtemperatur [ºC] | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysterese, Extrazone Temperatur [ºC] | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Blockierschutz Ventil
|  |  | Typ Blockierschutz | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Heizintervall [h] | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Heizintervall 2 [h] | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Kühlintervall [h] | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Kühlintervall 2 [h] | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Change-Over Intervall [h] | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | 6-Wege-Ventil Intervall [h] | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Heizdauer [s] | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Heizdauer 2 [s] | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Kühldauer [s] | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Kühldauer 2 [s] | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Change-Over Dauer [s] | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | 6-Wege-Ventil Dauer [s] | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analogeingänge
Temperatureingang
|  |  | Filterzeit [s] | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperatureingang 0-10 V
|  |  | Wert bei 0 V [°C] | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Wert bei 10 V [°C] | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2-Eingang
|  |  | Wert bei 0 V [ppm] | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Wert bei 10 V [ppm] | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filterzeit [s] | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Feuchteeingang
|  |  | Wert bei 0 V [%] | RH at 0 Volt input (RC_RH_0V)
|  |  | Wert bei 10 V [%] | RH at 10 Volt input (RC_RH_10V)
|  |  | Filterzeit [s] | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Volumenstromeingang
|  |  | Wert bei 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Wert bei 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filterzeit [s] | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC-Eingang
|  |  | Wert bei 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Wert bei 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filterzeit [s] | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Sollwerte
Raumsollwerte
|  |  | Heizen, Belegt [°C] | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Kühlen, Belegt [°C] | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Heizen, Standby [°C] | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Kühlen, Standby [°C] | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Heizen, Nicht belegt [°C] | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Kühlen, Nicht belegt [°C] | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Frostschutz [°C] | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Sollwertanpassung
|  |  | Max. Anpassung nach oben [°C] | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Max. Anpassung nach unten [°C] | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Sollwertanpassung [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Extrazone
|  |  | Extrazone Sollwert [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2-Sollwert [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Feuchte
|  |  | Feuchte Sollwert [%] | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC-Sollwert | Setpoint for VOC control (RC_VOCSetpoint)
Reglereinstellungen
Raum
|  |  | P-Band [°C] | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-Zeit [s] | I-time for room PID controller (RC_RoomPIDItime)
Kaskadenregelung
|  |  | Regelung aktiv | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Kaskadenfaktor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Max. Heiztemperatur [°C] | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min. Heiztemperatur [°C] | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Max. Kühltemperatur [°C] | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min. Kühltemperatur [°C] | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Frostschutztemperatur [°C] | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Extrazone
|  |  | P-Band [°C] | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-Zeit [s] | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-Band [ppm] | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-Zeit [s] | I-time for CO2 PID controller (RC_CO2PIDItime)
Feuchte
|  |  | P-Band [%] | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-Zeit [s] | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-Band | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-Zeit [s] | I-time for VOC PID controller (RC_VOCPIDItime)
Alarmeinstellungen
Raumtemperatur Alarm
|  |  | Oberer Grenzwert [°C] | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Unterer Grenzwert [°C] | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
CO2-Gehalt Alarm
|  |  | Oberer Grenzwert [ppm] | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Anpassungen Eingänge
UI1
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_2_offset)
Raumtemperatur
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_5_offset)
Raumfeuchte
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_6_offset)
VOC-Sensor
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_7_offset)
CO2-Fühler
|  |  | Grenzwert-Modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Offset-Anpassung | Offset for input (IoAnaIn_8_offset)
Anpassungen Ausgänge
UO1
|  |  | Minimalwert | Scale for output (IoAnaOut_1_min_in)
|  |  | Maximalwert | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maximalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_max_out)
|  |  | Offset bezogen auf Gesamtbereich [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Minimalwert | Scale for output (IoAnaOut_2_min_in)
|  |  | Maximalwert | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maximalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_max_out)
|  |  | Offset bezogen auf Gesamtbereich [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Minimalwert | Scale for output (IoAnaOut_3_min_in)
|  |  | Maximalwert | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maximalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_max_out)
|  |  | Offset bezogen auf Gesamtbereich [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Minimalwert | Scale for output (IoAnaOut_4_min_in)
|  |  | Maximalwert | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maximalwert [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_max_out)
|  |  | Offset bezogen auf Gesamtbereich [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_4_offset)
Hand/Auto
Ferneingabewerte
Raumtemperatur
|  |  | Ferneinstellung | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Einstellwert [°C] | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Raumtemperatur [°C] | Room temperature (RC_RoomTemp)
Zulufttemperatur
|  |  | Ferneinstellung | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Einstellwert [°C] | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Zulufttemperatur [°C] | Supply air temperature (RC_SupplyAirTemp)
Extrazone Temperatur
|  |  | Ferneinstellung | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Einstellwert [°C] | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Extrazone Temperatur [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
Change-Over Temperatur
|  |  | Ferneinstellung | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Einstellwert [°C] | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-Over Temperatur [°C] | Changeover temperature (RC_ChangeOverTemp)
Change-Over VVS Temperatur
|  |  | Ferneinstellung | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Einstellwert [°C] | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-Over VVS Temperatur [°C] | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2-Gehalt
|  |  | Ferneinstellung | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Einstellwert [ppm] | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2-Gehalt [ppm] | Room CO2 level (RC_CO2Level)
Raumfeuchte
|  |  | Ferneinstellung | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Einstellwert [%] | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Raumfeuchte [%] | Relative humidity (RC_Humidity)
Volumenstrom
|  |  | Ferneinstellung | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Einstellwert | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Volumenstrom | Air flow (RC_AirFlow)
VOC-Index
|  |  | Ferneinstellung | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Einstellwert | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC-Index | VOC index (RC_VOC)
Präsenzerkennung
|  |  | Ferneinstellung | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Einstellwert | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Präsenzerkennung | Presence indication (RC_Presence)
Offenes Fenster
|  |  | Ferneinstellung | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Einstellwert | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Offenes Fenster | Open window indication (RC_DIOpenWindow)
Kondensation
|  |  | Ferneinstellung | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Einstellwert | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Externer Alarm (DI)
|  |  | Ferneinstellung | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Einstellwert | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | Externer Alarm (DI) | Digital input alarm (RC_AlarmDI)
Change-Over DI
|  |  | Ferneinstellung | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Einstellwert | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-Over DI | Change-over digital input (RC_DIChangeOver)
Change-Over VVS DI
|  |  | Ferneinstellung | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Einstellwert | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-Over VVS DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Hand/Auto
Reglerstatus
|  |  | Reglerstatus | Current state (RC_ControllerState)
|  |  | Fernstatuseinstellung | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Ausschalten | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Zwangslüftung | Set controller in Bypass state (RC_ControllerStateSetBypass)
Ventilator Regelquelle
|  |  | Ventilator Regelquelle | Fan speed setting (RC_FanSelect)
Ausgang Heizen
|  |  | Betriebsmodus | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Einstellwert [%] | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Ausgang Heizen [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Betriebsmodus | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Ausgang Heizen | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Ausgang Heizen 2
|  |  | Betriebsmodus | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Einstellwert [%] | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Ausgang Heizen 2 [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Betriebsmodus | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Ausgang Heizen 2 | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Ausgang Kühlen
|  |  | Betriebsmodus | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Einstellwert [%] | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Ausgang Kühlen [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Betriebsmodus | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Ausgang Kühlen | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Ausgang Kühlen 2
|  |  | Betriebsmodus | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Einstellwert [%] | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Ausgang Kühlen 2 [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Betriebsmodus | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Ausgang Kühlen 2 | Room control Cool2 output digital (RC_RoomCool2OutputDO)
Ausgang VVS
|  |  | Betriebsmodus | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Einstellwert [%] | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | Ausgang VVS [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
Ausgang VVS 2
|  |  | Betriebsmodus | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Einstellwert [%] | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | Ausgang VVS 2 [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Ausgang Change-Over
|  |  | Betriebsmodus | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Einstellwert [%] | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Ausgang Change-Over [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Ausgang Change-Over VVS
|  |  | Betriebsmodus | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Einstellwert [%] | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Ausgang Change-Over VVS [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
Ausgang 6-Wege-Ventil
|  |  | Betriebsmodus | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Betriebsmodus | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Einstellwert [%] | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | Ausgang 6-Wege-Ventil [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Extrazone Ausgang
|  |  | Betriebsmodus | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Einstellwert [%] | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Extrazone Ausgang | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC-Ventilatorregelung
|  |  | Betriebsmodus | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Einstellwert [%] | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC-Ventilatorregelung [%] | Current EC fan speed (RC_ECFanSpeed)
CO2 Regelausgang
|  |  | Betriebsmodus | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Einstellwert [%] | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | CO2 Regelausgang [%] | CO2 control analog out (RC_CO2ControlAO)
Feuchte Regelausgang
|  |  | Betriebsmodus | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Einstellwert [%] | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Feuchte Regelausgang [%] | Humidify analog out (RC_HumidifyOutputAO)
Entfeuchter Regelausgang
|  |  | Betriebsmodus | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Einstellwert [%] | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Entfeuchter Regelausgang [%] | Dehumidify analog out (RC_DehumidifyOutputAO)
VOC Regelausgang
|  |  | Betriebsmodus | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Einstellwert [%] | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | VOC Regelausgang [%] | VOC control analog out (RC_VOCControlAO)
Extrazone aktiver Ausgang
|  |  | Betriebsmodus | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Extrazone aktiver Ausgang | Extra Zone active (RC_ExtraZoneActive)
Zwangslüftung Ausgang
|  |  | Betriebsmodus | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Zwangslüftung Ausgang | Forced ventilation output (RC_ForcedVentDO)
Hardwaresteuerung
UO1
|  |  | UO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Einstellwert [0=0 %, 100=100 %] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Einstellwert | Override value (IoDo_1_override)
UO2
|  |  | UO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Einstellwert [0=0 %, 100=100 %] | Override value (IoAnaOut_2_override)
|  |  | UO2: | Value set for output (IoDo_2_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Einstellwert | Override value (IoDo_2_override)
AO1
|  |  | AO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Einstellwert [0=0 %, 100=100 %] | Override value (IoAnaOut_3_override)
AO2
|  |  | AO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Einstellwert [0=0 %, 100=100 %] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Einstellwert | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Einstellwert | Override value (IoAnaIn_2_override)
Kalibrierung CO2-Fühler
|  |  | Automatische Selbstkalibrierung aktivieren | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Automatische Selbstkalibrierung Nullpunkt [ppm] [ppm] | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | CO2-Fühler erzwungene Neukalibrierung | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | CO2-Referenzwert für erzwungene Neukalibrierung [ppm] [ppm] | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Offset letzte erzwungene Neukalibrierung (-9999=Fehler) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | CO2-Fühler zurücksetzen | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Relaisausgang
|  |  | Status Relais | Value set for output (IoDo_3_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Einstellwert | Override value (IoDo_3_override)
PIR-Sensor
|  |  | PIR-Sensor | Filtered value from sensor (IoDiIn_4_value)
|  |  | Betriebsmodus | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Einstellwert | Override value (IoDiIn_4_override)
Gerät
Geräte-ID
Geräte-ID
|  |  | Name | (ControllerName)
|  |  | Beschreibung | Controller description (ControllerDescription)
|  |  | Standort | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Kommunikation
Porteinstellungen
|  |  | Port 1 Funktion | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Port 1 Baudrate | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Port 1 Parität | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbus-Adresse | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | BACnet MSTP Adresse | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | MSTP Max Master Adresse | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet Geräte-ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet Gerät Objektname | BACnet device object name (BACnetDeviceObjectName)
|  |  | Passwort | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth-Funktion | Function for BLE button (BleButtonMode)
|  |  | Ausschalten nach [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | BLE Sendeleistung | BLE TX power level (ble_power)
Kommunikationsausfall
|  |  | Fehler | Offline function (RC_OfflineFunction)
|  |  | Timeout [s] | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Fallback Status | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Zurücksetzen
Zurücksetzen
|  |  | Regler Neustart | Write to this register will trigger resets with different reset reasons (product_reset)
Nichtflüchtiger Speicher
Nichtflüchtiger Speicher
|  |  | Nichtflüchtigen Speicher deaktivieren | Set to 1 to disable storage in non volatile memory (disable_nv_storage)

## fr
RCX-2.1-1-01 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Tableau de bord
Vue d’ensemble
Système
|  |  | Régulateur | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Adresse Modbus | Active Modbus unit ID (ModbusUnitID)
|  |  | Adresse BACnet MSTP | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | ID bas BACnet | BACnet device ID (BACnetDeviceID)
|  |  | Total des alarmes | Sum Alarm (RC_SumAlarm)
Ambiance
|  |  | État du régulateur | Current state (RC_ControllerState)
|  |  | Mode | Current controller mode (RC_ControllerMode)
|  |  | Température d’ambiance [°C] | Room temperature (RC_RoomTemp)
|  |  | Température de soufflage [°C] | Supply air temperature (RC_SupplyAirTemp)
|  |  | Consigne d’ambiance [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Décalage de consigne [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Vitesse du ventilateur EC [%] | Current EC fan speed (RC_ECFanSpeed)
|  |  | Niveau de CO2 [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Humidité ambiante [%] | Relative humidity (RC_Humidity)
|  |  | Indice de COV | VOC index (RC_VOC)
|  |  | Détection de présence | Presence indication (RC_Presence)
|  |  | Condensation | Condensation indication (RC_DICondensation)
Zone supplémentaire
|  |  | Température de la zone supplémentaire [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Consigne zone supplémentaire [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Sortie zone supplémentaire active | Extra Zone active (RC_ExtraZoneActive)
Valeurs réelles
Séquence de contrôle d'ambiance
|  |  | Séquence 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Séquence 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Séquence 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Valeurs réelles
|  |  | Mode | Current controller mode (RC_ControllerMode)
|  |  | Température d’ambiance [°C] | Room temperature (RC_RoomTemp)
|  |  | Consigne d’ambiance [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Décalage de consigne [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Demande de chauffage [%] | Room PID heat output (RC_PIDHeatDemand)
|  |  | Demande de refroidissement [%] | Room PID cool output (RC_PIDCoolDemand)
|  |  | Sortie chauffage [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Sortie chauffage 2 [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Sortie refroidissement [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Sortie refroidissement 2 [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Sortie VAV [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | Sortie VAV 2 [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Température de change-over | Changeover temperature (RC_ChangeOverTemp)
|  |  | État du change-over | Change-over status (RC_ChangeOverState)
|  |  | Sortie change-over [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Température de change-over VAV | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | État du change-ove VAV | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Sortie VAV change-over [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | Sortie vanne 6 voies [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | Niveau de CO2 [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Consigne CO2 [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Sortie relais
|  |  | État du relais | Value set for output (IoDo_3_value)
Entrées/Sorties
Entrées universelles
|  |  | UI1 : | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1 : | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2 : | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2 : | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Sorties universelles
|  |  | UO1 : [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1 : | Value set for output (IoDo_1_value)
|  |  | UO2 : [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2 : | Value set for output (IoDo_2_value)
Sorties analogiques
|  |  | AO1 : [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2 : [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Sondes internes
|  |  | Température d’ambiance [°C] | Filtered value from sensor (IoAnaIn_5_value)
|  |  | Sonde de CO2 [ppm] | Filtered value from sensor (IoAnaIn_8_value)
|  |  | Sonde HR [%] | Filtered value from sensor (IoAnaIn_6_value)
|  |  | Sonde COV | Filtered value from sensor (IoAnaIn_7_value)
|  |  | Capteur PIR | Filtered value from sensor (IoDiIn_4_value)
Alarmes
Alarmes
|  |  | Total des alarmes | Sum Alarm (RC_SumAlarm)
|  |  | Erreur sonde | Sensor error alarm (RC_AlarmSensorError)
|  |  | Température ambiante haute | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Température ambiante basse | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | Niveau de CO2 élevé | High CO2 alarm (RC_AlarmCO2High)
|  |  | Alarme externe (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Sortie en mode manuel | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Code d’erreur de la sonde de température | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Code d’erreur de la sonde d’humidité | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | Code d'erreur de la sonde de COV | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | Code d'erreur de la sonde de CO2 | Detailed fault description (IoAnaIn_8_errorFlags)
À propos de…
ID d'appareil
|  |  | Nº de série | (SerialNumberString)
|  |  | Nom | (ControllerName)
|  |  | Description | Controller description (ControllerDescription)
|  |  | Emplacement | Controller location (ControllerLocation)
|  |  | Projet | (ControllerProject)
Menus personnalisés
Menu personnalisé 1
|  |  | Titre | Title for Custom Menu 1 (CM1Title)
|  |  | Valeur actuelle | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Alternative actuelle | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Alternative actuelle | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Alternative actuelle | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Alternative actuelle | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Alternative actuelle | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Alternative actuelle | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Alternative actuelle | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Alternative actuelle | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Alternative actuelle | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Alternative actuelle | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Alternative actuelle | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Alternative actuelle | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Alternative actuelle | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Alternative actuelle | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Alternative actuelle | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Alternative actuelle | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Alternative actuelle | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Alternative actuelle | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Alternative actuelle | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Alternative actuelle | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Alternative actuelle | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Indice de l'alternative actuelle | Current alternative for Custom Menu 1 (CM1CurrentAlt)
Menu personnalisé 2
|  |  | Titre | Title for Custom Menu 2 (CM2Title)
|  |  | Valeur actuelle | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Alternative actuelle | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Alternative actuelle | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Alternative actuelle | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Alternative actuelle | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Alternative actuelle | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Alternative actuelle | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Alternative actuelle | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Alternative actuelle | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Alternative actuelle | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Alternative actuelle | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Alternative actuelle | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Alternative actuelle | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Alternative actuelle | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Alternative actuelle | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Alternative actuelle | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Alternative actuelle | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Alternative actuelle | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Alternative actuelle | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Alternative actuelle | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Alternative actuelle | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Alternative actuelle | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Indice de l'alternative actuelle | Current alternative for Custom Menu 2 (CM2CurrentAlt)
Menu personnalisé 3
|  |  | Titre | Title for Custom Menu 3 (CM3Title)
|  |  | Valeur actuelle | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Alternative actuelle | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Alternative actuelle | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Alternative actuelle | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Alternative actuelle | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Alternative actuelle | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Alternative actuelle | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Alternative actuelle | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Alternative actuelle | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Alternative actuelle | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Alternative actuelle | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Alternative actuelle | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Alternative actuelle | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Alternative actuelle | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Alternative actuelle | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Alternative actuelle | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Alternative actuelle | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Alternative actuelle | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Alternative actuelle | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Alternative actuelle | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Alternative actuelle | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Alternative actuelle | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Indice de l'alternative actuelle | Current alternative for Custom Menu 3 (CM3CurrentAlt)
Menu personnalisé 4
|  |  | Titre | Title for Custom Menu 4 (CM4Title)
|  |  | Valeur actuelle | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Alternative actuelle | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Alternative actuelle | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Alternative actuelle | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Alternative actuelle | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Alternative actuelle | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Alternative actuelle | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Alternative actuelle | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Alternative actuelle | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Alternative actuelle | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Alternative actuelle | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Alternative actuelle | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Alternative actuelle | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Alternative actuelle | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Alternative actuelle | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Alternative actuelle | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Alternative actuelle | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Alternative actuelle | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Alternative actuelle | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Alternative actuelle | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Alternative actuelle | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Alternative actuelle | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Indice de l'alternative actuelle | Current alternative for Custom Menu 4 (CM4CurrentAlt)
Menu personnalisé 5
|  |  | Titre | Title for Custom Menu 5 (CM5Title)
|  |  | Valeur actuelle | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Alternative actuelle | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Alternative actuelle | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Alternative actuelle | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Alternative actuelle | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Alternative actuelle | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Alternative actuelle | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Alternative actuelle | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Alternative actuelle | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Alternative actuelle | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Alternative actuelle | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Alternative actuelle | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Alternative actuelle | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Alternative actuelle | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Alternative actuelle | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Alternative actuelle | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Alternative actuelle | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Alternative actuelle | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Alternative actuelle | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Alternative actuelle | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Alternative actuelle | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Alternative actuelle | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Indice de l'alternative actuelle | Current alternative for Custom Menu 5 (CM5CurrentAlt)
Menu personnalisé 6
|  |  | Titre | Title for Custom Menu 6 (CM6Title)
|  |  | Valeur actuelle | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Alternative actuelle | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Alternative actuelle | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Alternative actuelle | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Alternative actuelle | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Alternative actuelle | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Alternative actuelle | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Alternative actuelle | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Alternative actuelle | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Alternative actuelle | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Alternative actuelle | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Alternative actuelle | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Alternative actuelle | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Alternative actuelle | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Alternative actuelle | Text for alternative 14 for Custom Menu 6 (CM6Alt14Text)
|  |  | Alternative actuelle | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Alternative actuelle | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternative actuelle | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Alternative actuelle | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Alternative actuelle | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Alternative actuelle | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Alternative actuelle | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Indice de l'alternative actuelle | Current alternative for Custom Menu 6 (CM6CurrentAlt)
Menu personnalisé 7
|  |  | Titre | Title for Custom Menu 7 (CM7Title)
|  |  | Valeur actuelle | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Alternative actuelle | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Alternative actuelle | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Alternative actuelle | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Alternative actuelle | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Alternative actuelle | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Alternative actuelle | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Alternative actuelle | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Alternative actuelle | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Alternative actuelle | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Alternative actuelle | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Alternative actuelle | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Alternative actuelle | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Alternative actuelle | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Alternative actuelle | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Alternative actuelle | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Alternative actuelle | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Alternative actuelle | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Alternative actuelle | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Alternative actuelle | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Alternative actuelle | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Alternative actuelle | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Indice de l'alternative actuelle | Current alternative for Custom Menu 7 (CM7CurrentAlt)
Menu personnalisé 8
|  |  | Titre | Title for Custom Menu 8 (CM8Title)
|  |  | Valeur actuelle | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Alternative actuelle | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Alternative actuelle | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Alternative actuelle | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Alternative actuelle | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Alternative actuelle | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Alternative actuelle | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Alternative actuelle | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Alternative actuelle | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Alternative actuelle | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Alternative actuelle | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Alternative actuelle | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Alternative actuelle | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Alternative actuelle | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Alternative actuelle | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Alternative actuelle | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Alternative actuelle | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Alternative actuelle | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Alternative actuelle | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Alternative actuelle | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Alternative actuelle | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Alternative actuelle | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Indice de l'alternative actuelle | Current alternative for Custom Menu 8 (CM8CurrentAlt)
Configuration
Fonctions de contrôle
Séquence de contrôle d'ambiance
|  |  | Séquence 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Séquence 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Séquence 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Chauffage
|  |  | Limite max. [%] | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Limite min. [%] | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Temporisation d’arrêt du ventilateur batterie électrique | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Suivre l'état du change-over | Heat1 included in change-over function (RC_Heat1InChangeOver)
Chauffage 2
|  |  | Limite max. [%] | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Limite min. [%] | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Temporisation d’arrêt du ventilateur batterie électrique | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Suivre l'état du change-over | Heat2 included in change-over function (RC_Heat2InChangeOver)
Refroidissement
|  |  | Limite max. [%] | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Limite min. [%] | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Régler au maximum en mode ventilation forcée | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Désactiver la sortie lorsque le ventilateur est arrêté | Turn off Cool1 output when the fan is off (RC_Cool1OffWhenFanIsOff)
|  |  | Suivre l'état du change-over | Cool1 included in change-over function (RC_Cool1InChangeOver)
Refroidissement 2
|  |  | Limite max. [%] | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Limite min. [%] | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Régler au maximum en mode ventilation forcée | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Désactiver la sortie lorsque le ventilateur est arrêté | Turn off Cool2 output when the fan is off (RC_Cool2OffWhenFanIsOff)
|  |  | Suivre l'état du change-over | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Limite max. [%] | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Limite min., Arrêt [%] | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Limite min., inoccupé [%] | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Limite min., standby [%] | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Limite min., occupé [%] | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Limite min., ventilation forcée [%] | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Régler au maximum en mode ventilation forcée | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Limite max. en chauffage [%] | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Suivre l'état du change-over | VAV1 included in change-over function (RC_VAV1InChangeOver)
|  |  | Démarrer le VAV lorsque la séquence de refroidissement précédente est terminée [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Démarrer le VAV lorsque la séquence de chauffage précédente est terminée [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VAV 2
|  |  | Limite max. [%] | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Limite min., Arrêt [%] | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Limite min., inoccupé [%] | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Limite min., standby [%] | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Limite min., occupé [%] | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Limite min., ventilation forcée [%] | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Régler au maximum en mode ventilation forcée | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Limite max. en chauffage [%] | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Suivre l'état du change-over | VAV2 included in change-over function (RC_VAV2InChangeOver)
|  |  | Démarrer le VAV lorsque la séquence de refroidissement précédente est terminée [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Démarrer le VAV lorsque la séquence de chauffage précédente est terminée [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
Source de commande VAV
|  |  | Demande de refroidissement | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | Niveau de CO2 | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | Indice de COV | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Humidité | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Limite max. [%] | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Limite min. [%] | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Mode | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Température de change-over [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Hystérésis de chauffage [°C] | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Hystérésis de refroidissement [°C] | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Temporisation vanne [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over VAV
|  |  | Limite max. [%] | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Limite min., Arrêt [%] | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Limite min., inoccupé [%] | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Limite min., standby [%] | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Limite min., occupé [%] | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Limite min., ventilation forcée [%] | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Régler au maximum en mode ventilation forcée | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Mode | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Température de change-over [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Hystérésis de chauffage [°C] | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Hystérésis de refroidissement [°C] | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Temporisation vanne [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
|  |  | Démarrer le VAV lorsque la séquence de refroidissement précédente est terminée [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Démarrer le VAV lorsque la séquence de chauffage précédente est terminée [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
Vanne 6 voies
|  |  | Séq 1 totalement ouvert [V] | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Séq 1 début ouverture [V] | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Séq 2 totalement ouvert [V] | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Séq 2 début ouverture [V] | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Point central [V] | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Hystérésis du point central [%] | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Ordre séquence | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Suivre l'état du change-over | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
État du régulateur
|  |  | État préréglé | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | État à l'arrêt | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | État fenêtre ouverte | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Temps en mode ventilation forcée [min] | Bypass time (minutes) (RC_BypassTime)
Ventilation forcée
|  |  | Actif quand | Forced ventilation function (RC_ForcedVentMode)
|  |  | Limite de démarrage [%] | Forced ventilation start limit (RC_ForcedVentStartLimit)
Détection de présence
|  |  | État présence | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Temporisation activation [min] | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Temporisation désactivation [min] | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | Activation CO2 | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | Niveau de CO2 [ppm] | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | Hystérésis CO2 [ppm] | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Utiliser le PIR interne pour la présence | Use internal PIR sensor for presence detection (RC_PIRPresence)
Zone supplémentaire
Zone supplémentaire
|  |  | Fonction zone supplémentaire | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Désactivé en dessous de l’état | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Désactiver si le mode de zone principale diffère de la fonction | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Limite min. [%] | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Limite max. [%] | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Entrées/Sorties
Entrées universelles
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NF/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NF/NO | Invert logic signal (IoDiIn_2_invert)
Sorties universelles
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | Temps de cycle vanne thermique UO1 [s] | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NF/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | Signal de contrôle UO1 | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | Temps de cycle vanne thermique UO2 [s] | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NF/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | Signal de contrôle UO2 | Unit converter (IoAnaOut_2_unit)
Sorties analogiques
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | Signal de contrôle AO1 | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | Signal de contrôle AO2 | Unit converter (IoAnaOut_4_unit)
Contrôle ventilateurs
Source de contrôle ventilateur
|  |  | Contrôleur d’ambiance | Select fan control mode (RC_FanControlMode)
|  |  | Niveau de CO2 | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Humidité | Fan is controlled by humidity output (RC_FanControlHumidity)
Commande du ventilateur EC
|  |  | Vitesse sans demande | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Arrêt en dessous de la demande [%] | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hystérésis pour diminution de la vitesse du ventilateur [%] | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Vitesse de démarrage [%] | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Vitesse max. en mode automatique [%] | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Vitesse ventilation forcée | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Vitesse ventilation forcée [%] | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Sortie vitesse 1 [%] | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Sortie vitesse 2 [%] | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Sortie vitesse 3 [%] | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Protection moisissure | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Démarrage rapide ventilateur
|  |  | Durée du démarrage rapide [s] | Fan kick start time (RC_FanKickStartTime)
Délai d’arrêt ventilateur
|  |  | Délai d’arrêt [s] | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Vitesse minimale | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Boost ventilateur
|  |  | Mode | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Durée de boost [s] | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | Bande proportionnelle | Fan boost P band (RC_FanBoostPBand)
Affichage et menus
Affichage
|  |  | Écran d'accueil | What to display during device startup (DisplayStartupMode)
|  |  | Mode d’affichage | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Mode de consigne | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | Arrondir la valeur de CO2 au plus proche | Min step for CO2 value (RC_CO2Step)
|  |  | Luminosité totale [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Temporisation gradation, 0 = Toujours totale [s] | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Luminosité réduite [%] | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Temporisation, 0 = Jamais désactivé [s] | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Écran inactif
|  |  | Température/point de consigne | Show temperature/setpoint in idle view (App_IdleViewTemperature)
|  |  | Niveau de CO2 | Show CO2 value in idle view (App_IdleViewCO2)
|  |  | Humidité ambiante | Show humidity in idle view (App_IdleViewHumidity)
|  |  | Indice de COV | Show VOC in idle view (App_IdleViewVOC)
|  |  | État du régulateur | Show mode in idle view (App_IdleViewMode)
Menu
|  |  | Page réglage de consigne | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Page de menu Mode | Enable Mode menu page (App_EnableMenuMode)
|  |  | Page de menu Change-over | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Page de menu Ventilateur | Enable Fan menu page (App_EnableMenuFan)
|  |  | Page de menu Ventilation forcée | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Relance ventilation forcée | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Page température/point de consigne | Enable Temperature menu page (App_EnableMenuTemp)
|  |  | Page de menu Humidité | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | Page de menu CO2 | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | Page de menu COV | Enable VOC menu page (App_EnableMenuVOC)
Ordre d'affichage
|  |  | Position d’écran 1 | Display position 1 (DisplayPosition1)
|  |  | Position d’écran 2 | Display position 2 (DisplayPosition2)
|  |  | Position d’écran 3 | Display position 3 (DisplayPosition3)
|  |  | Position d’écran 4 | Display position 4 (DisplayPosition4)
|  |  | Position d’écran 5 | Display position 5 (DisplayPosition5)
|  |  | Position d’écran 6 | Display position 6 (DisplayPosition6)
|  |  | Position d’écran 7 | Display position 7 (DisplayPosition7)
|  |  | Position d’écran 8 | Display position 8 (DisplayPosition8)
|  |  | Position d’écran 9 | Display position 9 (DisplayPosition9)
|  |  | Position d’écran 10 | Display position 10 (DisplayPosition10)
|  |  | Position d’écran 11 | Display position 11 (DisplayPosition11)
|  |  | Position d’écran 12 | Display position 12 (DisplayPosition12)
Options de menu personnalisées
|  |  | Menu personnalisé 1 | Enable Custom Menu 1 (CM1Enabled)
|  |  | Menu personnalisé 2 | Enable Custom Menu 2 (CM2Enabled)
|  |  | Menu personnalisé 3 | Enable Custom Menu 3 (CM3Enabled)
|  |  | Menu personnalisé 4 | Enable Custom Menu 4 (CM4Enabled)
|  |  | Menu personnalisé 5 | Enable Custom Menu 5 (CM5Enabled)
|  |  | Menu personnalisé 6 | Enable Custom Menu 6 (CM6Enabled)
|  |  | Menu personnalisé 7 | Enable Custom Menu 7 (CM7Enabled)
|  |  | Menu personnalisé 8 | Enable Custom Menu 8 (CM8Enabled)
Options du menu Mode
|  |  | Texte du menu Titre | Mode menu title (App_ModeMenuTitle)
|  |  | Activation du mode Off | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Activation du mode Inoccupé | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Activation du mode Standby | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Activation du mode Occupé | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Activation du mode Ventilation forcée | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Texte du mode Off | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Texte du mode Inoccupé | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Texte du mode Standby | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Texte du mode Occupé | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Texte du mode Ventilation forcée | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Texte du mode Automatique | Mode menu Auto state text (App_ModeMenuAutoText)
Options du menu Change-over
|  |  | Texte du menu Titre | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | État Chauffage activé | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | État Refroidissement activé | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | État Auto activé | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | Texte de l'état Chauffage | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | Texte de l'état Refroidissement | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | Texte de l'état Auto | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
LED d'indication
|  |  | Luminosité [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Indication LED CO2 | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | LED jaune Niveau de CO2 [ppm] | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | LED rouge Niveau de CO2 [ppm] | CO2 level for red led (RC_CO2LevelRed)
Textes personnalisés
|  |  | Mode d’affichage | When to show the custom text (rt_text_visability)
|  |  | Mode d'affichage | Single or dual row text in display (rt_text_mode)
|  |  | Mode défilement | Scroll mode (rt_text_display_scroll_mode)
|  |  | Police | What font to use for the display text (rt_text_font)
|  |  | Délai de défilement [ms] | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Valeur de timer de texte personnalisé [s] | Time to show the custom text (rt_text_timeleft)
|  |  | Ligne de texte personnalisé 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Ligne de texte personnalisé 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Texte personnalisé 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Texte personnalisé 2 | String to show on row 2 in the display (rt_text_row_2)
Menus personnalisés
Menu personnalisé 1
|  |  | Titre | Title for Custom Menu 1 (CM1Title)
|  |  | Valeur actuelle | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Alternative 1 – Texte | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Alternative 1 – Valeur | Value for alternative 1 for Custom Menu 1 (CM1Alt1Value)
|  |  | Alternative 2 – Texte | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Alternative 2 – Valeur | Value for alternative 2 for Custom Menu 1 (CM1Alt2Value)
|  |  | Alternative 3 – Texte | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Alternative 3 – Valeur | Value for alternative 3 for Custom Menu 1 (CM1Alt3Value)
|  |  | Alternative 4 – Texte | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Alternative 4 – Valeur | Value for alternative 4 for Custom Menu 1 (CM1Alt4Value)
|  |  | Alternative 5 – Texte | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Alternative 5 – Valeur | Value for alternative 5 for Custom Menu 1 (CM1Alt5Value)
|  |  | Alternative 6 – Texte | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Alternative 6 – Valeur | Value for alternative 6 for Custom Menu 1 (CM1Alt6Value)
|  |  | Alternative 7 – Texte | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Alternative 7 – Valeur | Value for alternative 7 for Custom Menu 1 (CM1Alt7Value)
|  |  | Alternative 8 – Texte | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Alternative 8 – Valeur | Value for alternative 8 for Custom Menu 1 (CM1Alt8Value)
|  |  | Alternative 9 – Texte | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Alternative 9 – Valeur | Value for alternative 9 for Custom Menu 1 (CM1Alt9Value)
|  |  | Alternative 10 – Texte | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Alternative 10 – Valeur | Value for alternative 10 for Custom Menu 1 (CM1Alt10Value)
|  |  | Alternative 11 – Texte | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Alternative 11 – Valeur | Value for alternative 11 for Custom Menu 1 (CM1Alt11Value)
|  |  | Alternative 12 – Texte | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Alternative 12 – Valeur | Value for alternative 12 for Custom Menu 1 (CM1Alt12Value)
|  |  | Alternative 13 – Texte | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Alternative 13 – Valeur | Value for alternative 13 for Custom Menu 1 (CM1Alt13Value)
|  |  | Alternative 14 – Texte | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Alternative 14 – Valeur | Value for alternative 14 for Custom Menu 1 (CM1Alt14Value)
|  |  | Alternative 15 – Texte | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Alternative 15 – Valeur | Value for alternative 15 for Custom Menu 1 (CM1Alt15Value)
|  |  | Alternative 16 – Texte | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Alternative 16 – Valeur | Value for alternative 16 for Custom Menu 1 (CM1Alt16Value)
|  |  | Alternative 17 – Texte | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Alternative 17 – Valeur | Value for alternative 17 for Custom Menu 1 (CM1Alt17Value)
|  |  | Alternative 18 – Texte | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Alternative 18 – Valeur | Value for alternative 18 for Custom Menu 1 (CM1Alt18Value)
|  |  | Alternative 19 – Texte | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Alternative 19 – Valeur | Value for alternative 19 for Custom Menu 1 (CM1Alt19Value)
|  |  | Alternative 20 – Texte | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Alternative 20 – Valeur | Value for alternative 20 for Custom Menu 1 (CM1Alt20Value)
|  |  | Alternative 21 – Texte | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Alternative 21 – Valeur | Value for alternative 21 for Custom Menu 1 (CM1Alt21Value)
Menu personnalisé 2
|  |  | Titre | Title for Custom Menu 2 (CM2Title)
|  |  | Valeur actuelle | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Alternative 1 – Texte | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Alternative 1 – Valeur | Value for alternative 1 for Custom Menu 2 (CM2Alt1Value)
|  |  | Alternative 2 – Texte | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Alternative 2 – Valeur | Value for alternative 2 for Custom Menu 2 (CM2Alt2Value)
|  |  | Alternative 3 – Texte | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Alternative 3 – Valeur | Value for alternative 3 for Custom Menu 2 (CM2Alt3Value)
|  |  | Alternative 4 – Texte | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Alternative 4 – Valeur | Value for alternative 4 for Custom Menu 2 (CM2Alt4Value)
|  |  | Alternative 5 – Texte | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Alternative 5 – Valeur | Value for alternative 5 for Custom Menu 2 (CM2Alt5Value)
|  |  | Alternative 6 – Texte | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Alternative 6 – Valeur | Value for alternative 6 for Custom Menu 2 (CM2Alt6Value)
|  |  | Alternative 7 – Texte | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Alternative 7 – Valeur | Value for alternative 7 for Custom Menu 2 (CM2Alt7Value)
|  |  | Alternative 8 – Texte | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Alternative 8 – Valeur | Value for alternative 8 for Custom Menu 2 (CM2Alt8Value)
|  |  | Alternative 9 – Texte | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Alternative 9 – Valeur | Value for alternative 9 for Custom Menu 2 (CM2Alt9Value)
|  |  | Alternative 10 – Texte | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Alternative 10 – Valeur | Value for alternative 10 for Custom Menu 2 (CM2Alt10Value)
|  |  | Alternative 11 – Texte | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Alternative 11 – Valeur | Value for alternative 11 for Custom Menu 2 (CM2Alt11Value)
|  |  | Alternative 12 – Texte | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Alternative 12 – Valeur | Value for alternative 12 for Custom Menu 2 (CM2Alt12Value)
|  |  | Alternative 13 – Texte | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Alternative 13 – Valeur | Value for alternative 13 for Custom Menu 2 (CM2Alt13Value)
|  |  | Alternative 14 – Texte | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Alternative 14 – Valeur | Value for alternative 14 for Custom Menu 2 (CM2Alt14Value)
|  |  | Alternative 15 – Texte | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Alternative 15 – Valeur | Value for alternative 15 for Custom Menu 2 (CM2Alt15Value)
|  |  | Alternative 16 – Texte | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Alternative 16 – Valeur | Value for alternative 16 for Custom Menu 2 (CM2Alt16Value)
|  |  | Alternative 17 – Texte | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Alternative 17 – Valeur | Value for alternative 17 for Custom Menu 2 (CM2Alt17Value)
|  |  | Alternative 18 – Texte | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Alternative 18 – Valeur | Value for alternative 18 for Custom Menu 2 (CM2Alt18Value)
|  |  | Alternative 19 – Texte | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Alternative 19 – Valeur | Value for alternative 19 for Custom Menu 2 (CM2Alt19Value)
|  |  | Alternative 20 – Texte | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Alternative 20 – Valeur | Value for alternative 20 for Custom Menu 2 (CM2Alt20Value)
|  |  | Alternative 21 – Texte | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Alternative 21 – Valeur | Value for alternative 21 for Custom Menu 2 (CM2Alt21Value)
Menu personnalisé 3
|  |  | Titre | Title for Custom Menu 3 (CM3Title)
|  |  | Valeur actuelle | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Alternative 1 – Texte | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Alternative 1 – Valeur | Value for alternative 1 for Custom Menu 3 (CM3Alt1Value)
|  |  | Alternative 2 – Texte | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Alternative 2 – Valeur | Value for alternative 2 for Custom Menu 3 (CM3Alt2Value)
|  |  | Alternative 3 – Texte | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Alternative 3 – Valeur | Value for alternative 3 for Custom Menu 3 (CM3Alt3Value)
|  |  | Alternative 4 – Texte | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Alternative 4 – Valeur | Value for alternative 4 for Custom Menu 3 (CM3Alt4Value)
|  |  | Alternative 5 – Texte | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Alternative 5 – Valeur | Value for alternative 5 for Custom Menu 3 (CM3Alt5Value)
|  |  | Alternative 6 – Texte | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Alternative 6 – Valeur | Value for alternative 6 for Custom Menu 3 (CM3Alt6Value)
|  |  | Alternative 7 – Texte | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Alternative 7 – Valeur | Value for alternative 7 for Custom Menu 3 (CM3Alt7Value)
|  |  | Alternative 8 – Texte | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Alternative 8 – Valeur | Value for alternative 8 for Custom Menu 3 (CM3Alt8Value)
|  |  | Alternative 9 – Texte | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Alternative 9 – Valeur | Value for alternative 9 for Custom Menu 3 (CM3Alt9Value)
|  |  | Alternative 10 – Texte | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Alternative 10 – Valeur | Value for alternative 10 for Custom Menu 3 (CM3Alt10Value)
|  |  | Alternative 11 – Texte | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Alternative 11 – Valeur | Value for alternative 11 for Custom Menu 3 (CM3Alt11Value)
|  |  | Alternative 12 – Texte | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Alternative 12 – Valeur | Value for alternative 12 for Custom Menu 3 (CM3Alt12Value)
|  |  | Alternative 13 – Texte | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Alternative 13 – Valeur | Value for alternative 13 for Custom Menu 3 (CM3Alt13Value)
|  |  | Alternative 14 – Texte | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Alternative 14 – Valeur | Value for alternative 14 for Custom Menu 3 (CM3Alt14Value)
|  |  | Alternative 15 – Texte | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Alternative 15 – Valeur | Value for alternative 15 for Custom Menu 3 (CM3Alt15Value)
|  |  | Alternative 16 – Texte | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Alternative 16 – Valeur | Value for alternative 16 for Custom Menu 3 (CM3Alt16Value)
|  |  | Alternative 17 – Texte | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Alternative 17 – Valeur | Value for alternative 17 for Custom Menu 3 (CM3Alt17Value)
|  |  | Alternative 18 – Texte | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Alternative 18 – Valeur | Value for alternative 18 for Custom Menu 3 (CM3Alt18Value)
|  |  | Alternative 19 – Texte | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Alternative 19 – Valeur | Value for alternative 19 for Custom Menu 3 (CM3Alt19Value)
|  |  | Alternative 20 – Texte | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Alternative 20 – Valeur | Value for alternative 20 for Custom Menu 3 (CM3Alt20Value)
|  |  | Alternative 21 – Texte | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Alternative 21 – Valeur | Value for alternative 21 for Custom Menu 3 (CM3Alt21Value)
Menu personnalisé 4
|  |  | Titre | Title for Custom Menu 4 (CM4Title)
|  |  | Valeur actuelle | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Alternative 1 – Texte | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Alternative 1 – Valeur | Value for alternative 1 for Custom Menu 4 (CM4Alt1Value)
|  |  | Alternative 2 – Texte | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Alternative 2 – Valeur | Value for alternative 2 for Custom Menu 4 (CM4Alt2Value)
|  |  | Alternative 3 – Texte | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Alternative 3 – Valeur | Value for alternative 3 for Custom Menu 4 (CM4Alt3Value)
|  |  | Alternative 4 – Texte | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Alternative 4 – Valeur | Value for alternative 4 for Custom Menu 4 (CM4Alt4Value)
|  |  | Alternative 5 – Texte | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Alternative 5 – Valeur | Value for alternative 5 for Custom Menu 4 (CM4Alt5Value)
|  |  | Alternative 6 – Texte | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Alternative 6 – Valeur | Value for alternative 6 for Custom Menu 4 (CM4Alt6Value)
|  |  | Alternative 7 – Texte | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Alternative 7 – Valeur | Value for alternative 7 for Custom Menu 4 (CM4Alt7Value)
|  |  | Alternative 8 – Texte | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Alternative 8 – Valeur | Value for alternative 8 for Custom Menu 4 (CM4Alt8Value)
|  |  | Alternative 9 – Texte | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Alternative 9 – Valeur | Value for alternative 9 for Custom Menu 4 (CM4Alt9Value)
|  |  | Alternative 10 – Texte | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Alternative 10 – Valeur | Value for alternative 10 for Custom Menu 4 (CM4Alt10Value)
|  |  | Alternative 11 – Texte | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Alternative 11 – Valeur | Value for alternative 11 for Custom Menu 4 (CM4Alt11Value)
|  |  | Alternative 12 – Texte | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Alternative 12 – Valeur | Value for alternative 12 for Custom Menu 4 (CM4Alt12Value)
|  |  | Alternative 13 – Texte | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Alternative 13 – Valeur | Value for alternative 13 for Custom Menu 4 (CM4Alt13Value)
|  |  | Alternative 14 – Texte | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Alternative 14 – Valeur | Value for alternative 14 for Custom Menu 4 (CM4Alt14Value)
|  |  | Alternative 15 – Texte | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Alternative 15 – Valeur | Value for alternative 15 for Custom Menu 4 (CM4Alt15Value)
|  |  | Alternative 16 – Texte | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Alternative 16 – Valeur | Value for alternative 16 for Custom Menu 4 (CM4Alt16Value)
|  |  | Alternative 17 – Texte | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Alternative 17 – Valeur | Value for alternative 17 for Custom Menu 4 (CM4Alt17Value)
|  |  | Alternative 18 – Texte | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Alternative 18 – Valeur | Value for alternative 18 for Custom Menu 4 (CM4Alt18Value)
|  |  | Alternative 19 – Texte | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Alternative 19 – Valeur | Value for alternative 19 for Custom Menu 4 (CM4Alt19Value)
|  |  | Alternative 20 – Texte | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Alternative 20 – Valeur | Value for alternative 20 for Custom Menu 4 (CM4Alt20Value)
|  |  | Alternative 21 – Texte | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Alternative 21 – Valeur | Value for alternative 21 for Custom Menu 4 (CM4Alt21Value)
Menu personnalisé 5
|  |  | Titre | Title for Custom Menu 5 (CM5Title)
|  |  | Valeur actuelle | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Alternative 1 – Texte | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Alternative 1 – Valeur | Value for alternative 1 for Custom Menu 5 (CM5Alt1Value)
|  |  | Alternative 2 – Texte | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Alternative 2 – Valeur | Value for alternative 2 for Custom Menu 5 (CM5Alt2Value)
|  |  | Alternative 3 – Texte | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Alternative 3 – Valeur | Value for alternative 3 for Custom Menu 5 (CM5Alt3Value)
|  |  | Alternative 4 – Texte | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Alternative 4 – Valeur | Value for alternative 4 for Custom Menu 5 (CM5Alt4Value)
|  |  | Alternative 5 – Texte | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Alternative 5 – Valeur | Value for alternative 5 for Custom Menu 5 (CM5Alt5Value)
|  |  | Alternative 6 – Texte | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Alternative 6 – Valeur | Value for alternative 6 for Custom Menu 5 (CM5Alt6Value)
|  |  | Alternative 7 – Texte | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Alternative 7 – Valeur | Value for alternative 7 for Custom Menu 5 (CM5Alt7Value)
|  |  | Alternative 8 – Texte | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Alternative 8 – Valeur | Value for alternative 8 for Custom Menu 5 (CM5Alt8Value)
|  |  | Alternative 9 – Texte | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Alternative 9 – Valeur | Value for alternative 9 for Custom Menu 5 (CM5Alt9Value)
|  |  | Alternative 10 – Texte | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Alternative 10 – Valeur | Value for alternative 10 for Custom Menu 5 (CM5Alt10Value)
|  |  | Alternative 11 – Texte | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Alternative 11 – Valeur | Value for alternative 11 for Custom Menu 5 (CM5Alt11Value)
|  |  | Alternative 12 – Texte | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Alternative 12 – Valeur | Value for alternative 12 for Custom Menu 5 (CM5Alt12Value)
|  |  | Alternative 13 – Texte | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Alternative 13 – Valeur | Value for alternative 13 for Custom Menu 5 (CM5Alt13Value)
|  |  | Alternative 14 – Texte | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Alternative 14 – Valeur | Value for alternative 14 for Custom Menu 5 (CM5Alt14Value)
|  |  | Alternative 15 – Texte | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Alternative 15 – Valeur | Value for alternative 15 for Custom Menu 5 (CM5Alt15Value)
|  |  | Alternative 16 – Texte | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Alternative 16 – Valeur | Value for alternative 16 for Custom Menu 5 (CM5Alt16Value)
|  |  | Alternative 17 – Texte | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Alternative 17 – Valeur | Value for alternative 17 for Custom Menu 5 (CM5Alt17Value)
|  |  | Alternative 18 – Texte | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Alternative 18 – Valeur | Value for alternative 18 for Custom Menu 5 (CM5Alt18Value)
|  |  | Alternative 19 – Texte | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Alternative 19 – Valeur | Value for alternative 19 for Custom Menu 5 (CM5Alt19Value)
|  |  | Alternative 20 – Texte | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Alternative 20 – Valeur | Value for alternative 20 for Custom Menu 5 (CM5Alt20Value)
|  |  | Alternative 21 – Texte | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Alternative 21 – Valeur | Value for alternative 21 for Custom Menu 5 (CM5Alt21Value)
Menu personnalisé 6
|  |  | Titre | Title for Custom Menu 6 (CM6Title)
|  |  | Valeur actuelle | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Alternative 1 – Texte | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Alternative 1 – Valeur | Value for alternative 1 for Custom Menu 6 (CM6Alt1Value)
|  |  | Alternative 2 – Texte | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Alternative 2 – Valeur | Value for alternative 2 for Custom Menu 6 (CM6Alt2Value)
|  |  | Alternative 3 – Texte | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Alternative 3 – Valeur | Value for alternative 3 for Custom Menu 6 (CM6Alt3Value)
|  |  | Alternative 4 – Texte | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Alternative 4 – Valeur | Value for alternative 4 for Custom Menu 6 (CM6Alt4Value)
|  |  | Alternative 5 – Texte | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Alternative 5 – Valeur | Value for alternative 5 for Custom Menu 6 (CM6Alt5Value)
|  |  | Alternative 6 – Texte | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Alternative 6 – Valeur | Value for alternative 6 for Custom Menu 6 (CM6Alt6Value)
|  |  | Alternative 7 – Texte | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Alternative 7 – Valeur | Value for alternative 7 for Custom Menu 6 (CM6Alt7Value)
|  |  | Alternative 8 – Texte | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Alternative 8 – Valeur | Value for alternative 8 for Custom Menu 6 (CM6Alt8Value)
|  |  | Alternative 9 – Texte | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Alternative 9 – Valeur | Value for alternative 9 for Custom Menu 6 (CM6Alt9Value)
|  |  | Alternative 10 – Texte | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Alternative 10 – Valeur | Value for alternative 10 for Custom Menu 6 (CM6Alt10Value)
|  |  | Alternative 11 – Texte | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Alternative 11 – Valeur | Value for alternative 11 for Custom Menu 6 (CM6Alt11Value)
|  |  | Alternative 12 – Texte | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Alternative 12 – Valeur | Value for alternative 12 for Custom Menu 6 (CM6Alt12Value)
|  |  | Alternative 13 – Texte | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Alternative 13 – Valeur | Value for alternative 13 for Custom Menu 6 (CM6Alt13Value)
|  |  | Alternative 14 – Texte | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternative 14 – Valeur | Value for alternative 14 for Custom Menu 6 (CM6Alt14Value)
|  |  | Alternative 15 – Texte | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Alternative 15 – Valeur | Value for alternative 15 for Custom Menu 6 (CM6Alt15Value)
|  |  | Alternative 16 – Texte | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternative 16 – Valeur | Value for alternative 16 for Custom Menu 6 (CM6Alt16Value)
|  |  | Alternative 17 – Texte | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Alternative 17 – Valeur | Value for alternative 17 for Custom Menu 6 (CM6Alt17Value)
|  |  | Alternative 18 – Texte | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Alternative 18 – Valeur | Value for alternative 18 for Custom Menu 6 (CM6Alt18Value)
|  |  | Alternative 19 – Texte | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Alternative 19 – Valeur | Value for alternative 19 for Custom Menu 6 (CM6Alt19Value)
|  |  | Alternative 20 – Texte | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Alternative 20 – Valeur | Value for alternative 20 for Custom Menu 6 (CM6Alt20Value)
|  |  | Alternative 21 – Texte | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Alternative 21 – Valeur | Value for alternative 21 for Custom Menu 6 (CM6Alt21Value)
Menu personnalisé 7
|  |  | Titre | Title for Custom Menu 7 (CM7Title)
|  |  | Valeur actuelle | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Alternative 1 – Texte | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Alternative 1 – Valeur | Value for alternative 1 for Custom Menu 7 (CM7Alt1Value)
|  |  | Alternative 2 – Texte | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Alternative 2 – Valeur | Value for alternative 2 for Custom Menu 7 (CM7Alt2Value)
|  |  | Alternative 3 – Texte | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Alternative 3 – Valeur | Value for alternative 3 for Custom Menu 7 (CM7Alt3Value)
|  |  | Alternative 4 – Texte | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Alternative 4 – Valeur | Value for alternative 4 for Custom Menu 7 (CM7Alt4Value)
|  |  | Alternative 5 – Texte | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Alternative 5 – Valeur | Value for alternative 5 for Custom Menu 7 (CM7Alt5Value)
|  |  | Alternative 6 – Texte | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Alternative 6 – Valeur | Value for alternative 6 for Custom Menu 7 (CM7Alt6Value)
|  |  | Alternative 7 – Texte | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Alternative 7 – Valeur | Value for alternative 7 for Custom Menu 7 (CM7Alt7Value)
|  |  | Alternative 8 – Texte | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Alternative 8 – Valeur | Value for alternative 8 for Custom Menu 7 (CM7Alt8Value)
|  |  | Alternative 9 – Texte | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Alternative 9 – Valeur | Value for alternative 9 for Custom Menu 7 (CM7Alt9Value)
|  |  | Alternative 10 – Texte | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Alternative 10 – Valeur | Value for alternative 10 for Custom Menu 7 (CM7Alt10Value)
|  |  | Alternative 11 – Texte | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Alternative 11 – Valeur | Value for alternative 11 for Custom Menu 7 (CM7Alt11Value)
|  |  | Alternative 12 – Texte | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Alternative 12 – Valeur | Value for alternative 12 for Custom Menu 7 (CM7Alt12Value)
|  |  | Alternative 13 – Texte | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Alternative 13 – Valeur | Value for alternative 13 for Custom Menu 7 (CM7Alt13Value)
|  |  | Alternative 14 – Texte | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Alternative 14 – Valeur | Value for alternative 14 for Custom Menu 7 (CM7Alt14Value)
|  |  | Alternative 15 – Texte | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Alternative 15 – Valeur | Value for alternative 15 for Custom Menu 7 (CM7Alt15Value)
|  |  | Alternative 16 – Texte | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Alternative 16 – Valeur | Value for alternative 16 for Custom Menu 7 (CM7Alt16Value)
|  |  | Alternative 17 – Texte | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Alternative 17 – Valeur | Value for alternative 17 for Custom Menu 7 (CM7Alt17Value)
|  |  | Alternative 18 – Texte | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Alternative 18 – Valeur | Value for alternative 18 for Custom Menu 7 (CM7Alt18Value)
|  |  | Alternative 19 – Texte | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Alternative 19 – Valeur | Value for alternative 19 for Custom Menu 7 (CM7Alt19Value)
|  |  | Alternative 20 – Texte | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Alternative 20 – Valeur | Value for alternative 20 for Custom Menu 7 (CM7Alt20Value)
|  |  | Alternative 21 – Texte | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Alternative 21 – Valeur | Value for alternative 21 for Custom Menu 7 (CM7Alt21Value)
Menu personnalisé 8
|  |  | Titre | Title for Custom Menu 8 (CM8Title)
|  |  | Valeur actuelle | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Alternative 1 – Texte | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Alternative 1 – Valeur | Value for alternative 1 for Custom Menu 8 (CM8Alt1Value)
|  |  | Alternative 2 – Texte | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Alternative 2 – Valeur | Value for alternative 2 for Custom Menu 8 (CM8Alt2Value)
|  |  | Alternative 3 – Texte | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Alternative 3 – Valeur | Value for alternative 3 for Custom Menu 8 (CM8Alt3Value)
|  |  | Alternative 4 – Texte | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Alternative 4 – Valeur | Value for alternative 4 for Custom Menu 8 (CM8Alt4Value)
|  |  | Alternative 5 – Texte | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Alternative 5 – Valeur | Value for alternative 5 for Custom Menu 8 (CM8Alt5Value)
|  |  | Alternative 6 – Texte | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Alternative 6 – Valeur | Value for alternative 6 for Custom Menu 8 (CM8Alt6Value)
|  |  | Alternative 7 – Texte | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Alternative 7 – Valeur | Value for alternative 7 for Custom Menu 8 (CM8Alt7Value)
|  |  | Alternative 8 – Texte | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Alternative 8 – Valeur | Value for alternative 8 for Custom Menu 8 (CM8Alt8Value)
|  |  | Alternative 9 – Texte | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Alternative 9 – Valeur | Value for alternative 9 for Custom Menu 8 (CM8Alt9Value)
|  |  | Alternative 10 – Texte | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Alternative 10 – Valeur | Value for alternative 10 for Custom Menu 8 (CM8Alt10Value)
|  |  | Alternative 11 – Texte | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Alternative 11 – Valeur | Value for alternative 11 for Custom Menu 8 (CM8Alt11Value)
|  |  | Alternative 12 – Texte | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Alternative 12 – Valeur | Value for alternative 12 for Custom Menu 8 (CM8Alt12Value)
|  |  | Alternative 13 – Texte | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Alternative 13 – Valeur | Value for alternative 13 for Custom Menu 8 (CM8Alt13Value)
|  |  | Alternative 14 – Texte | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Alternative 14 – Valeur | Value for alternative 14 for Custom Menu 8 (CM8Alt14Value)
|  |  | Alternative 15 – Texte | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Alternative 15 – Valeur | Value for alternative 15 for Custom Menu 8 (CM8Alt15Value)
|  |  | Alternative 16 – Texte | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Alternative 16 – Valeur | Value for alternative 16 for Custom Menu 8 (CM8Alt16Value)
|  |  | Alternative 17 – Texte | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Alternative 17 – Valeur | Value for alternative 17 for Custom Menu 8 (CM8Alt17Value)
|  |  | Alternative 18 – Texte | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Alternative 18 – Valeur | Value for alternative 18 for Custom Menu 8 (CM8Alt18Value)
|  |  | Alternative 19 – Texte | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Alternative 19 – Valeur | Value for alternative 19 for Custom Menu 8 (CM8Alt19Value)
|  |  | Alternative 20 – Texte | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Alternative 20 – Valeur | Value for alternative 20 for Custom Menu 8 (CM8Alt20Value)
|  |  | Alternative 21 – Texte | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Alternative 21 – Valeur | Value for alternative 21 for Custom Menu 8 (CM8Alt21Value)
Actionneurs
Sorties On/Off
|  |  | Hystérésis de chauffage, température ambiante [ºC] | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Hystérésis de refroidissement, température ambiante [ºC] | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hystérésis, température de zone supplémentaire [ºC] | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Exercice de vanne
|  |  | Exercice de vannes | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Intervalle de chauffage [h] | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Intervalle chauffage 2 [h] | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Intervalle de refroidissement [h] | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Intervalle de refroidissement 2 [h] | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Intervalle change-over [h] | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | Intervalle vanne 6 voies [h] | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Durée chauffage [s] | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Durée chauffage 2 [s] | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Durée refroidissement [s] | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Durée refroidissement 2 [s] | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Durée change-over [s] | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | Durée vanne 6 voies [s] | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Entrées analogiques
Entrée température
|  |  | Temps de filtrage [s] | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Entrée température 0-10V
|  |  | Valeur à 0 V [°C] | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Valeur à 10 V [°C] | Room temperature at 10 Volt input (RC_RoomTemp_10V)
Entrée CO2
|  |  | Valeur à 0 V [ppm] | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Valeur à 10 V [ppm] | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Temps de filtrage [s] | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Entrée humidité
|  |  | Valeur à 0 V [%] | RH at 0 Volt input (RC_RH_0V)
|  |  | Valeur à 10 V [%] | RH at 10 Volt input (RC_RH_10V)
|  |  | Temps de filtrage [s] | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Entrée débit
|  |  | Valeur à 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Valeur à 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Temps de filtrage [s] | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
Entrée COV
|  |  | Valeur à 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Valeur à 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Temps de filtrage [s] | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Points de consigne
Consignes d’ambiance
|  |  | Chauffage, occupé [°C] | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Refroidissement, occupé [°C] | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Chauffage, standby [°C] | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Refroidissement, standby [°C] | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Chauffage, inoccupé [°C] | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Refroidissement, inoccupé [°C] | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Protection antigel [°C] | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Décalage de consigne
|  |  | Réglage max. vers le haut [°C] | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Réglage max. vers le bas [°C] | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Décalage de consigne [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Zone supplémentaire
|  |  | Consigne zone supplémentaire [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | Consigne CO2 [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Humidité
|  |  | Consigne humidité [%] | Setpoint Humidity control (RC_HumiditySetpoint)
COV
|  |  | Consigne COV | Setpoint for VOC control (RC_VOCSetpoint)
Réglages du régulateur
Ambiance
|  |  | Bande proportionnelle [°C] | P-band for room PID controller (RC_RoomPIDPband)
|  |  | Temps d’intégration [s] | I-time for room PID controller (RC_RoomPIDItime)
Contrôle en cascade
|  |  | Contrôle activé | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Facteur de cascade | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Température de chauffage max. [°C] | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Température de chauffage min. [°C] | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Température de refroidissement max. [°C] | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Température de refroidissement min. [°C] | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Température protection antigel [°C] | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Zone supplémentaire
|  |  | Bande proportionnelle [°C] | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | Temps d’intégration [s] | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | Bande proportionnelle [ppm] | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | Temps d’intégration [s] | I-time for CO2 PID controller (RC_CO2PIDItime)
Humidité
|  |  | Bande proportionnelle [%] | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | Temps d’intégration [s] | I-time for Humidity PID controller (RC_HumidityPIDItime)
COV
|  |  | Bande proportionnelle | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | Temps d’intégration [s] | I-time for VOC PID controller (RC_VOCPIDItime)
Réglage des alarmes
Alarme température ambiante
|  |  | Limite haute [°C] | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Limite basse [°C] | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
Alarme de niveau de CO2
|  |  | Limite haute [ppm] | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Réglages des entrées
UI1
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_2_offset)
Température d’ambiance
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_5_offset)
Humidité ambiante
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_6_offset)
Sonde COV
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_7_offset)
Sonde de CO2
|  |  | Mode Limites | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Ajustement du décalage | Offset for input (IoAnaIn_8_offset)
Réglages de sortie
UO1
|  |  | Valeur minimale | Scale for output (IoAnaOut_1_min_in)
|  |  | Valeur maximale | Scale for output (IoAnaOut_1_max_in)
|  |  | Valeur minimale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_min_out)
|  |  | Valeur maximale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_1_max_out)
|  |  | Décalage basé sur la plage complète [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Valeur minimale | Scale for output (IoAnaOut_2_min_in)
|  |  | Valeur maximale | Scale for output (IoAnaOut_2_max_in)
|  |  | Valeur minimale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_min_out)
|  |  | Valeur maximale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_2_max_out)
|  |  | Décalage basé sur la plage complète [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Valeur minimale | Scale for output (IoAnaOut_3_min_in)
|  |  | Valeur maximale | Scale for output (IoAnaOut_3_max_in)
|  |  | Valeur minimale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_min_out)
|  |  | Valeur maximale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_3_max_out)
|  |  | Décalage basé sur la plage complète [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Valeur minimale | Scale for output (IoAnaOut_4_min_in)
|  |  | Valeur maximale | Scale for output (IoAnaOut_4_max_in)
|  |  | Valeur minimale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_min_out)
|  |  | Valeur maximale [0=0 %, 100=100 %] | Scale for output (IoAnaOut_4_max_out)
|  |  | Décalage basé sur la plage complète [-100=-100 %, 100=100 %] | Offset for output (IoAnaOut_4_offset)
Manuel/Auto
Valeurs des entrées distantes
Température d’ambiance
|  |  | Commande à distance | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Valeur réglée [°C] | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Température d’ambiance [°C] | Room temperature (RC_RoomTemp)
Température de soufflage
|  |  | Commande à distance | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Valeur réglée [°C] | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Température de soufflage [°C] | Supply air temperature (RC_SupplyAirTemp)
Température de la zone supplémentaire
|  |  | Commande à distance | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Valeur réglée [°C] | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Température de la zone supplémentaire [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
Température de change-over
|  |  | Commande à distance | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Valeur réglée [°C] | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Température de change-over [°C] | Changeover temperature (RC_ChangeOverTemp)
Température de change-over VAV
|  |  | Commande à distance | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Valeur réglée [°C] | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Température de change-over VAV [°C] | Changeover VAV temperature (RC_ChangeOverVAVTemp)
Niveau de CO2
|  |  | Commande à distance | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Valeur réglée [ppm] | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | Niveau de CO2 [ppm] | Room CO2 level (RC_CO2Level)
Humidité ambiante
|  |  | Commande à distance | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Valeur réglée [%] | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Humidité ambiante [%] | Relative humidity (RC_Humidity)
Débit d’air
|  |  | Commande à distance | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Valeur réglée | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Débit d’air | Air flow (RC_AirFlow)
Indice de COV
|  |  | Commande à distance | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Valeur réglée | Remote setting of VOC index (RC_VOCRemote)
|  |  | Indice de COV | VOC index (RC_VOC)
Détection de présence
|  |  | Commande à distance | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Valeur réglée | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Détection de présence | Presence indication (RC_Presence)
Fenêtre ouverte
|  |  | Commande à distance | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Valeur réglée | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Fenêtre ouverte | Open window indication (RC_DIOpenWindow)
Condensation
|  |  | Commande à distance | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Valeur réglée | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Condensation | Condensation indication (RC_DICondensation)
Alarme externe (DI)
|  |  | Commande à distance | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Valeur réglée | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | Alarme externe (DI) | Digital input alarm (RC_AlarmDI)
DI Change-over
|  |  | Commande à distance | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Valeur réglée | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | DI Change-over | Change-over digital input (RC_DIChangeOver)
DI Change-over VAV
|  |  | Commande à distance | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Valeur réglée | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | DI Change-over VAV | Change-over VAV digital input (RC_DIChangeOverVAV)
Manuel/Auto
État du régulateur
|  |  | État du régulateur | Current state (RC_ControllerState)
|  |  | Réglage commande à distance | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Arrêt | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Ventilation forcée | Set controller in Bypass state (RC_ControllerStateSetBypass)
Source de contrôle ventilateur
|  |  | Source de contrôle ventilateur | Fan speed setting (RC_FanSelect)
Sortie chauffage
|  |  | Mode | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Sortie chauffage [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Mode | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Sortie chauffage | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Sortie chauffage 2
|  |  | Mode | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Sortie chauffage 2 [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Mode | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Sortie chauffage 2 | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Sortie refroidissement
|  |  | Mode | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Sortie refroidissement [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Mode | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Sortie refroidissement | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Sortie refroidissement 2
|  |  | Mode | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Sortie refroidissement 2 [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Mode | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Sortie refroidissement 2 | Room control Cool2 output digital (RC_RoomCool2OutputDO)
Sortie VAV
|  |  | Mode | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | Sortie VAV [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
Sortie VAV 2
|  |  | Mode | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | Sortie VAV 2 [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Sortie change-over
|  |  | Mode | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Sortie change-over [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Sortie VAV change-over
|  |  | Mode | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Sortie VAV change-over [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
Sortie vanne 6 voies
|  |  | Mode | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Mode | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Valeur réglée [%] | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | Sortie vanne 6 voies [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Sortie zone supplémentaire
|  |  | Mode | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Sortie zone supplémentaire | Extra Zone output analog (RC_ExtraZoneOutputAO)
Commande du ventilateur EC
|  |  | Mode | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Valeur réglée [%] | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | Commande du ventilateur EC [%] | Current EC fan speed (RC_ECFanSpeed)
Sortie contrôle CO2
|  |  | Mode | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Valeur réglée [%] | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | Sortie contrôle CO2 [%] | CO2 control analog out (RC_CO2ControlAO)
Sortie contrôle d’humidification
|  |  | Mode | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Sortie contrôle d’humidification [%] | Humidify analog out (RC_HumidifyOutputAO)
Sortie contrôle de déshumidification
|  |  | Mode | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Valeur réglée [%] | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Sortie contrôle de déshumidification [%] | Dehumidify analog out (RC_DehumidifyOutputAO)
Sortie contrôle COV
|  |  | Mode | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Valeur réglée [%] | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | Sortie contrôle COV [%] | VOC control analog out (RC_VOCControlAO)
Sortie zone supplémentaire active
|  |  | Mode | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Sortie zone supplémentaire active | Extra Zone active (RC_ExtraZoneActive)
Sortie ventilation forcée
|  |  | Mode | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Sortie ventilation forcée | Forced ventilation output (RC_ForcedVentDO)
Contrôle des sorties physiques
UO1
|  |  | UO1 : [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Valeur définie [0=0 %, 100=100 %] | Override value (IoAnaOut_1_override)
|  |  | UO1 : | Value set for output (IoDo_1_value)
|  |  | Mode | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Valeur réglée | Override value (IoDo_1_override)
UO2
|  |  | UO2 : [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Valeur définie [0=0 %, 100=100 %] | Override value (IoAnaOut_2_override)
|  |  | UO2 : | Value set for output (IoDo_2_value)
|  |  | Mode | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Valeur réglée | Override value (IoDo_2_override)
AO1
|  |  | AO1 : [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Valeur définie [0=0 %, 100=100 %] | Override value (IoAnaOut_3_override)
AO2
|  |  | AO2 : [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Valeur définie [0=0 %, 100=100 %] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1 : | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Valeur réglée | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2 : | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Valeur réglée | Override value (IoAnaIn_2_override)
Étalonnage de la sonde CO2
|  |  | Activer autocalibrage automatique | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Référence autocalibrage automatique [ppm] [ppm] | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | Exécuter un réétalonnage forcé de la sonde CO2 | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | Niveau de CO2 de référence pour le réétalonnage forcé [ppm] [ppm] | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Dernier décalage de réétalonnage forcé (-9999 = Erreur) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | Réinitialiser la sonde CO2 | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Sortie relais
|  |  | État du relais | Value set for output (IoDo_3_value)
|  |  | Mode | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Valeur réglée | Override value (IoDo_3_override)
Capteur PIR
|  |  | Capteur PIR | Filtered value from sensor (IoDiIn_4_value)
|  |  | Mode | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Valeur réglée | Override value (IoDiIn_4_override)
Appareil
ID d'appareil
ID d'appareil
|  |  | Nom | (ControllerName)
|  |  | Description | Controller description (ControllerDescription)
|  |  | Emplacement | Controller location (ControllerLocation)
|  |  | Projet | (ControllerProject)
Communication
Réglages du port
|  |  | Fonction Port 1 | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Vitesse de transmission Port 1 | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Parité Port 1 | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Adresse Modbus | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | Adresse BACnet MSTP | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | Adresse maître MSTP max. | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | ID bas BACnet | BACnet device ID (BACnetDeviceID)
|  |  | Nom d’objet de l’appareil BACnet | BACnet device object name (BACnetDeviceObjectName)
|  |  | Mot de passe | BACnet password (BACnetPassword)
Bluetooth
|  |  | Fonction Bluetooth | Function for BLE button (BleButtonMode)
|  |  | Arrêter après [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | Puissance d’émission BLE | BLE TX power level (ble_power)
Défaut de communication
|  |  | Action en cas d’échec | Offline function (RC_OfflineFunction)
|  |  | Délai Expiré [s] | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | État de secours | State to set during communication faults (RC_ControllerStateFail)
|  |  | État | Heartbeat function indicates if the device is offline or not (RC_Offline)
Reset
Reset
|  |  | Redémarrer régulateur | Write to this register will trigger resets with different reset reasons (product_reset)
Stockage non volatil
Stockage non volatil
|  |  | Désactiver le stockage non volatil | Set to 1 to disable storage in non volatile memory (disable_nv_storage)

## nl
RCX-2.1-1-01 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Overzicht
Systeem
|  |  | Regelaar | Model number (Model)
|  |  | Versie | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbus adres | Active Modbus unit ID (ModbusUnitID)
|  |  | BACnet MSTP adres | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet apparaat ID | BACnet device ID (BACnetDeviceID)
|  |  | Verzamel alarm | Sum Alarm (RC_SumAlarm)
Ruimte
|  |  | Regelaar status | Current state (RC_ControllerState)
|  |  | Modus | Current controller mode (RC_ControllerMode)
|  |  | Ruimte temperatuur [°C] | Room temperature (RC_RoomTemp)
|  |  | Inblaas temperatuur [°C] | Supply air temperature (RC_SupplyAirTemp)
|  |  | Ruimte gewenst [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Gewenste verstelling [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC ventilator snelheid [%] | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2 niveau [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Ruimte vochtigheid [%] | Relative humidity (RC_Humidity)
|  |  | VOC-index | VOC index (RC_VOC)
|  |  | Aanwezigheid detector | Presence indication (RC_Presence)
|  |  | Condensatie | Condensation indication (RC_DICondensation)
Extra zone
|  |  | Extra zone temperatuur [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Extra zone gewenst [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Extra zone actief uitgang | Extra Zone active (RC_ExtraZoneActive)
Huidige waarden
Ruimte regelaar volgorde
|  |  | Volgorde 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Volgorde 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Volgorde 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Huidige waarden
|  |  | Modus | Current controller mode (RC_ControllerMode)
|  |  | Ruimte temperatuur [°C] | Room temperature (RC_RoomTemp)
|  |  | Ruimte gewenst [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Gewenste verstelling [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Verwarmvraag [%] | Room PID heat output (RC_PIDHeatDemand)
|  |  | Koelvraag [%] | Room PID cool output (RC_PIDCoolDemand)
|  |  | Verwarming uitgang [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Verwarming 2 uitgang [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Koeling uitgang [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Koeling 2 uitgang [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | VAV uitgang [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | VAV 2 uitgang [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-over temperatuur | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-over status | Change-over status (RC_ChangeOverState)
|  |  | Change-over uitgang [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-over VAV temperatuur | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-over VAV status | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Change-over VAV uitgang [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | 6-wegklep uitgang [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2 niveau [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2 gewenst [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Relais uitgang
|  |  | Relais status | Value set for output (IoDo_3_value)
Ingangen/Uitgangen
Universele ingangen
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universele uitgangen
|  |  | UO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analoge uitgangen
|  |  | AO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Interne sensoren
|  |  | Ruimte temperatuur [°C] | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2 sensor [ppm] | Filtered value from sensor (IoAnaIn_8_value)
|  |  | RV sensor [%] | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC sensor | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR sensor | Filtered value from sensor (IoDiIn_4_value)
Alarmen
Alarmen
|  |  | Verzamel alarm | Sum Alarm (RC_SumAlarm)
|  |  | Defecte opnemer | Sensor error alarm (RC_AlarmSensorError)
|  |  | Hoge ruimte temperatuur | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Lage ruimte temperatuur | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | Hoog CO2-gehalte | High CO2 alarm (RC_AlarmCO2High)
|  |  | Extern alarm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Uitgang in handbediening | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Foutcode temperatuuropnemer | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Foutcode vochtigheidsopnemer | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | Foutcode VOC sensor | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | Foutcode CO2 sensor | Detailed fault description (IoAnaIn_8_errorFlags)
Info
Apparaat-ID
|  |  | Serienummer | (SerialNumberString)
|  |  | Naam | (ControllerName)
|  |  | Omschrijving | Controller description (ControllerDescription)
|  |  | Locatie | Controller location (ControllerLocation)
|  |  | Project | (ControllerProject)
Aangepaste menu's
Aangepast menu 1
|  |  | Titel | Title for Custom Menu 1 (CM1Title)
|  |  | Actuele waarde | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Actuele alternatief | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Actuele alternatief | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Actuele alternatief | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Actuele alternatief | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Actuele alternatief | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Actuele alternatief | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Actuele alternatief | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Actuele alternatief | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Actuele alternatief | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Actuele alternatief | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Actuele alternatief | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Actuele alternatief | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Actuele alternatief | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Actuele alternatief | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Actuele alternatief | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Actuele alternatief | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Actuele alternatief | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Actuele alternatief | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Actuele alternatief | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Actuele alternatief | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Actuele alternatief | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Actuele alternatief index | Current alternative for Custom Menu 1 (CM1CurrentAlt)
Aangepast menu 2
|  |  | Titel | Title for Custom Menu 2 (CM2Title)
|  |  | Actuele waarde | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Actuele alternatief | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Actuele alternatief | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Actuele alternatief | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Actuele alternatief | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Actuele alternatief | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Actuele alternatief | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Actuele alternatief | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Actuele alternatief | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Actuele alternatief | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Actuele alternatief | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Actuele alternatief | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Actuele alternatief | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Actuele alternatief | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Actuele alternatief | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Actuele alternatief | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Actuele alternatief | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Actuele alternatief | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Actuele alternatief | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Actuele alternatief | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Actuele alternatief | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Actuele alternatief | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Actuele alternatief index | Current alternative for Custom Menu 2 (CM2CurrentAlt)
Aangepast menu 3
|  |  | Titel | Title for Custom Menu 3 (CM3Title)
|  |  | Actuele waarde | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Actuele alternatief | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Actuele alternatief | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Actuele alternatief | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Actuele alternatief | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Actuele alternatief | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Actuele alternatief | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Actuele alternatief | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Actuele alternatief | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Actuele alternatief | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Actuele alternatief | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Actuele alternatief | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Actuele alternatief | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Actuele alternatief | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Actuele alternatief | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Actuele alternatief | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Actuele alternatief | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Actuele alternatief | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Actuele alternatief | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Actuele alternatief | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Actuele alternatief | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Actuele alternatief | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Actuele alternatief index | Current alternative for Custom Menu 3 (CM3CurrentAlt)
Aangepast menu 4
|  |  | Titel | Title for Custom Menu 4 (CM4Title)
|  |  | Actuele waarde | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Actuele alternatief | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Actuele alternatief | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Actuele alternatief | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Actuele alternatief | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Actuele alternatief | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Actuele alternatief | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Actuele alternatief | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Actuele alternatief | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Actuele alternatief | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Actuele alternatief | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Actuele alternatief | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Actuele alternatief | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Actuele alternatief | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Actuele alternatief | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Actuele alternatief | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Actuele alternatief | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Actuele alternatief | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Actuele alternatief | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Actuele alternatief | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Actuele alternatief | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Actuele alternatief | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Actuele alternatief index | Current alternative for Custom Menu 4 (CM4CurrentAlt)
Aangepast menu 5
|  |  | Titel | Title for Custom Menu 5 (CM5Title)
|  |  | Actuele waarde | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Actuele alternatief | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Actuele alternatief | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Actuele alternatief | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Actuele alternatief | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Actuele alternatief | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Actuele alternatief | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Actuele alternatief | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Actuele alternatief | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Actuele alternatief | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Actuele alternatief | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Actuele alternatief | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Actuele alternatief | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Actuele alternatief | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Actuele alternatief | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Actuele alternatief | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Actuele alternatief | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Actuele alternatief | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Actuele alternatief | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Actuele alternatief | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Actuele alternatief | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Actuele alternatief | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Actuele alternatief index | Current alternative for Custom Menu 5 (CM5CurrentAlt)
Aangepast menu 6
|  |  | Titel | Title for Custom Menu 6 (CM6Title)
|  |  | Actuele waarde | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Actuele alternatief | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Actuele alternatief | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Actuele alternatief | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Actuele alternatief | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Actuele alternatief | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Actuele alternatief | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Actuele alternatief | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Actuele alternatief | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Actuele alternatief | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Actuele alternatief | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Actuele alternatief | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Actuele alternatief | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Actuele alternatief | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Actuele alternatief | Text for alternative 14 for Custom Menu 6 (CM6Alt14Text)
|  |  | Actuele alternatief | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Actuele alternatief | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Actuele alternatief | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Actuele alternatief | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Actuele alternatief | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Actuele alternatief | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Actuele alternatief | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Actuele alternatief index | Current alternative for Custom Menu 6 (CM6CurrentAlt)
Aangepast menu 7
|  |  | Titel | Title for Custom Menu 7 (CM7Title)
|  |  | Actuele waarde | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Actuele alternatief | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Actuele alternatief | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Actuele alternatief | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Actuele alternatief | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Actuele alternatief | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Actuele alternatief | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Actuele alternatief | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Actuele alternatief | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Actuele alternatief | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Actuele alternatief | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Actuele alternatief | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Actuele alternatief | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Actuele alternatief | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Actuele alternatief | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Actuele alternatief | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Actuele alternatief | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Actuele alternatief | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Actuele alternatief | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Actuele alternatief | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Actuele alternatief | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Actuele alternatief | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Actuele alternatief index | Current alternative for Custom Menu 7 (CM7CurrentAlt)
Aangepast menu 8
|  |  | Titel | Title for Custom Menu 8 (CM8Title)
|  |  | Actuele waarde | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Actuele alternatief | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Actuele alternatief | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Actuele alternatief | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Actuele alternatief | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Actuele alternatief | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Actuele alternatief | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Actuele alternatief | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Actuele alternatief | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Actuele alternatief | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Actuele alternatief | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Actuele alternatief | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Actuele alternatief | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Actuele alternatief | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Actuele alternatief | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Actuele alternatief | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Actuele alternatief | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Actuele alternatief | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Actuele alternatief | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Actuele alternatief | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Actuele alternatief | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Actuele alternatief | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Actuele alternatief index | Current alternative for Custom Menu 8 (CM8CurrentAlt)
Configuratie
Regel functies
Ruimte regelaar volgorde
|  |  | Volgorde 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Volgorde 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Volgorde 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Verwarming
|  |  | Max. limiet [%] | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min. limiet [%] | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Uitschakelvertraging ventilator voor elektrische verwarming | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Volg change-over status | Heat1 included in change-over function (RC_Heat1InChangeOver)
Verwarming 2
|  |  | Max. limiet [%] | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min. limiet [%] | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Uitschakelvertraging ventilator voor elektrische verwarming | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Volg change-over status | Heat2 included in change-over function (RC_Heat2InChangeOver)
Koeling
|  |  | Max. limiet [%] | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min. limiet [%] | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Ingesteld op max. bij geforceerde ventilatie | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Uitgang uitschakelen wanneer ventilator uit is | Turn off Cool1 output when the fan is off (RC_Cool1OffWhenFanIsOff)
|  |  | Volg change-over status | Cool1 included in change-over function (RC_Cool1InChangeOver)
Koeling 2
|  |  | Max. limiet [%] | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min. limiet [%] | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Ingesteld op max. bij geforceerde ventilatie | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Uitgang uitschakelen wanneer ventilator uit is | Turn off Cool2 output when the fan is off (RC_Cool2OffWhenFanIsOff)
|  |  | Volg change-over status | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Max. limiet [%] | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min. limiet, uit [%] | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min. limiet, afwezig [%] | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min. limiet, stand-by [%] | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min. limiet, aanwezig [%] | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min. limiet, geforceerde ventilatie [%] | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Ingesteld op max. bij geforceerde ventilatie | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Max. limiet bij verwarmen [%] | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Volg change-over status | VAV1 included in change-over function (RC_VAV1InChangeOver)
|  |  | Start VAV wanneer vorige koel volgorde bereikt is [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Start VAV wanneer vorige verwarming volgorde bereikt is [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VAV 2
|  |  | Max. limiet [%] | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min. limiet, uit [%] | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min. limiet, afwezig [%] | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min. limiet, stand-by [%] | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min. limiet, aanwezig [%] | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min. limiet, geforceerde ventilatie [%] | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Ingesteld op max. bij geforceerde ventilatie | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Max. limiet bij verwarmen [%] | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Volg change-over status | VAV2 included in change-over function (RC_VAV2InChangeOver)
|  |  | Start VAV wanneer vorige koel volgorde bereikt is [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Start VAV wanneer vorige verwarming volgorde bereikt is [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VAV-regelingen
|  |  | Koelvraag | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2 niveau | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC-index | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Vochtigheid | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Max. limiet [%] | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min. limiet [%] | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Modus | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-over temperatuur [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Verwarming hysterese [°C] | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Koel hysterese [°C] | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Vertragingstijd klep [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over VAV
|  |  | Max. limiet [%] | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min. limiet, uit [%] | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min. limiet, afwezig [%] | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min. limiet, stand-by [%] | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min. limiet, aanwezig [%] | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min. limiet, geforceerde ventilatie [%] | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Ingesteld op max. bij geforceerde ventilatie | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Modus | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-over temperatuur [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Verwarming hysterese [°C] | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Koel hysterese [°C] | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Vertragingstijd klep [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
|  |  | Start VAV wanneer vorige koel volgorde bereikt is [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Start VAV wanneer vorige verwarming volgorde bereikt is [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
6-weg klep
|  |  | Volg 1 volledig open [V] | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Volg 1 start openen [V] | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Volg 2 volledig open [V] | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Volg 2 start openen [V] | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Centraal punt [V] | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Centraal punt hysterese [%] | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Volgorde | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Volg change-over status | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Regelaar status
|  |  | Ingeschakelde regelaar status | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Uitgeschakelde regelaar status | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Raam open | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Tijd in geforceerde ventilatiemodus [min] | Bypass time (minutes) (RC_BypassTime)
Geforceerde ventilatie
|  |  | Actief wanneer | Forced ventilation function (RC_ForcedVentMode)
|  |  | Start limiet [%] | Forced ventilation start limit (RC_ForcedVentStartLimit)
Aanwezigheid detector
|  |  | Actuele status | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Vertraging actief [min] | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Vertraging inactief [min] | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2 activering | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2 niveau [ppm] | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2 hysterese [ppm] | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Gebruik interne PIR voor aanwezigheid | Use internal PIR sensor for presence detection (RC_PIRPresence)
Extra zone
Extra zone
|  |  | Extra zone functie | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Uitschakelen als status lager dan | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Uitschakelen als hoofdzonemodus afwijkt van functie | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min. limiet [%] | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Max. limiet [%] | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Ingangen/Uitgangen
Universele ingangen
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universele uitgangen
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | U01 periode thermische klep [s] | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | U01 regelsignaal | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | U02 periode thermische klep [s] | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | U02 regelsignaal | Unit converter (IoAnaOut_2_unit)
Analoge uitgangen
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO1 regelsignaal | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | AO2 regelsignaal | Unit converter (IoAnaOut_4_unit)
Ventilator regeling
Ventilator regeling
|  |  | Ruimte regelaar | Select fan control mode (RC_FanControlMode)
|  |  | CO2 niveau | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Vochtigheid | Fan is controlled by humidity output (RC_FanControlHumidity)
EC Ventilator regeling
|  |  | Snelheid bij geen vraag | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Uit onder de vraag [%] | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysterese voor ventilator snelheid verlagen [%] | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Start snelheid [%] | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Max. snelheid in automodus [%] | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Snelheid geforceerde ventilatie | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Snelheid geforceerde ventilatie [%] | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Snelheid 1 uitgang [%] | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Snelheid 2 uitgang [%] | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Snelheid 3 uitgang [%] | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Vorm beveiliging | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Kick-start ventilator
|  |  | Kick-start tijd [s] | Fan kick start time (RC_FanKickStartTime)
Vertraging ventilator uit
|  |  | Uit vertraging tijd [s] | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Minimum snelheid | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Ventilatorboost
|  |  | Modus | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Boost tijd [s] | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-band | Fan boost P band (RC_FanBoostPBand)
Display en menu's
Display
|  |  | Start scherm | What to display during device startup (DisplayStartupMode)
|  |  | Display weergave | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Display weergave bij waarde wijziging | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | CO2-waarde afronden | Min step for CO2 value (RC_CO2Step)
|  |  | Helderheid hoog [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Tijdsduur hoog, 0 = Altijd aan [s] | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Helderheid laag [%] | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Tijdsduur laag, 0 = Nooit uit [s] | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Start weergave
|  |  | Temperatuur/gewenst | Show temperature/setpoint in idle view (App_IdleViewTemperature)
|  |  | CO2 niveau | Show CO2 value in idle view (App_IdleViewCO2)
|  |  | Ruimte vochtigheid | Show humidity in idle view (App_IdleViewHumidity)
|  |  | VOC-index | Show VOC in idle view (App_IdleViewVOC)
|  |  | Regelaar status | Show mode in idle view (App_IdleViewMode)
Menu
|  |  | Instellen van gewenste waarden pagina | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Menu pagina modus | Enable Mode menu page (App_EnableMenuMode)
|  |  | Change-over menu pagina | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Ventilator menu pagina | Enable Fan menu page (App_EnableMenuFan)
|  |  | Geforceerde ventilatie menu pagina | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Geforceerde ventilatie overwerktimer | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Temperatuur/gewenste waarde pagina | Enable Temperature menu page (App_EnableMenuTemp)
|  |  | Vochtigheid menu pagina | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | CO2 menu pagina | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | VOC menu pagina | Enable VOC menu page (App_EnableMenuVOC)
Volgorde weergave
|  |  | Weergavepositie 1 | Display position 1 (DisplayPosition1)
|  |  | Weergavepositie 2 | Display position 2 (DisplayPosition2)
|  |  | Weergavepositie 3 | Display position 3 (DisplayPosition3)
|  |  | Weergavepositie 4 | Display position 4 (DisplayPosition4)
|  |  | Weergavepositie 5 | Display position 5 (DisplayPosition5)
|  |  | Weergavepositie 6 | Display position 6 (DisplayPosition6)
|  |  | Weergavepositie 7 | Display position 7 (DisplayPosition7)
|  |  | Weergavepositie 8 | Display position 8 (DisplayPosition8)
|  |  | Weergavepositie 9 | Display position 9 (DisplayPosition9)
|  |  | Weergavepositie 10 | Display position 10 (DisplayPosition10)
|  |  | Weergavepositie 11 | Display position 11 (DisplayPosition11)
|  |  | Weergavepositie 12 | Display position 12 (DisplayPosition12)
Aangepaste menu-opties
|  |  | Aangepast menu 1 | Enable Custom Menu 1 (CM1Enabled)
|  |  | Aangepast menu 2 | Enable Custom Menu 2 (CM2Enabled)
|  |  | Aangepast menu 3 | Enable Custom Menu 3 (CM3Enabled)
|  |  | Aangepast menu 4 | Enable Custom Menu 4 (CM4Enabled)
|  |  | Aangepast menu 5 | Enable Custom Menu 5 (CM5Enabled)
|  |  | Aangepast menu 6 | Enable Custom Menu 6 (CM6Enabled)
|  |  | Aangepast menu 7 | Enable Custom Menu 7 (CM7Enabled)
|  |  | Aangepast menu 8 | Enable Custom Menu 8 (CM8Enabled)
Modus menu-opties
|  |  | Menu titel tekst | Mode menu title (App_ModeMenuTitle)
|  |  | Modus Uit inschakelen | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Modus Afwezig inschakelen | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Modus Stand-by inschakelen | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Modus Aanwezig inschakelen | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Modus Geforceerde ventilatie inschakelen | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Modus Uit tekst | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Modus Afwezig tekst | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Modus Stand-by tekst | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Modus Aanwezig tekst | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Modus Geforceerde ventilatie tekst | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Modus Auto tekst | Mode menu Auto state text (App_ModeMenuAutoText)
Change-over menu-opties
|  |  | Menu titel tekst | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | Status Verwarming inschakelen | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | Status Koeling inschakelen | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | Status Auto inschakelen | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | Status Verwarming tekst | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | Status Koeling tekst | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | Status Auto tekst | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
Led-indicatie
|  |  | Helderheid [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 led-indicatie | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Gele led CO2-niveau [ppm] | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Rode led CO2-niveau [ppm] | CO2 level for red led (RC_CO2LevelRed)
Aangepaste teksten
|  |  | Display weergave | When to show the custom text (rt_text_visability)
|  |  | Display modus | Single or dual row text in display (rt_text_mode)
|  |  | Scroll modus | Scroll mode (rt_text_display_scroll_mode)
|  |  | Lettertype | What font to use for the display text (rt_text_font)
|  |  | Scroll vertraging [ms] | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Aangepaste tekst timerwaarde [s] | Time to show the custom text (rt_text_timeleft)
|  |  | Aangepaste tekst rij 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Aangepaste tekst rij 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Aangepaste tekst 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Aangepaste tekst 2 | String to show on row 2 in the display (rt_text_row_2)
Aangepaste menu's
Aangepast menu 1
|  |  | Titel | Title for Custom Menu 1 (CM1Title)
|  |  | Actuele waarde | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Alternatief 1 - Tekst | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Alternatief 1 - Waarde | Value for alternative 1 for Custom Menu 1 (CM1Alt1Value)
|  |  | Alternatief 2 - Tekst | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Alternatief 2 - Waarde | Value for alternative 2 for Custom Menu 1 (CM1Alt2Value)
|  |  | Alternatief 3 - Tekst | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Alternatief 3 - Waarde | Value for alternative 3 for Custom Menu 1 (CM1Alt3Value)
|  |  | Alternatief 4 - Tekst | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Alternatief 4 - Waarde | Value for alternative 4 for Custom Menu 1 (CM1Alt4Value)
|  |  | Alternatief 5 - Tekst | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Alternatief 5 - Waarde | Value for alternative 5 for Custom Menu 1 (CM1Alt5Value)
|  |  | Alternatief 6 – Tekst | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Alternatief 6 - Waarde | Value for alternative 6 for Custom Menu 1 (CM1Alt6Value)
|  |  | Alternatief 7 – Tekst | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Alternatief 7 - Waarde | Value for alternative 7 for Custom Menu 1 (CM1Alt7Value)
|  |  | Alternatief 8 – Tekst | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Alternatief 8 - Waarde | Value for alternative 8 for Custom Menu 1 (CM1Alt8Value)
|  |  | Alternatief 9 – Tekst | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Alternatief 9 - Waarde | Value for alternative 9 for Custom Menu 1 (CM1Alt9Value)
|  |  | Alternatief 10 – Tekst | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Alternatief 10 – Waarde | Value for alternative 10 for Custom Menu 1 (CM1Alt10Value)
|  |  | Alternatief 11 – Tekst | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Alternatief 11 - Waarde | Value for alternative 11 for Custom Menu 1 (CM1Alt11Value)
|  |  | Alternatief 12 – Tekst | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Alternatief 12 - Waarde | Value for alternative 12 for Custom Menu 1 (CM1Alt12Value)
|  |  | Alternatief 13 – Tekst | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Alternatief 13 – Waarde | Value for alternative 13 for Custom Menu 1 (CM1Alt13Value)
|  |  | Alternatief 14 – Tekst | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Alternatief 14- Waarde | Value for alternative 14 for Custom Menu 1 (CM1Alt14Value)
|  |  | Alternatief 15 – Tekst | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Alternatief 15 – Waarde | Value for alternative 15 for Custom Menu 1 (CM1Alt15Value)
|  |  | Alternatief 16 – Tekst | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Alternatief 16 – Waarde | Value for alternative 16 for Custom Menu 1 (CM1Alt16Value)
|  |  | Alternatief 17 – Tekst | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Alternatief 17 – Waarde | Value for alternative 17 for Custom Menu 1 (CM1Alt17Value)
|  |  | Alternatief 18 – Tekst | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Alternatief 18 - Waarde | Value for alternative 18 for Custom Menu 1 (CM1Alt18Value)
|  |  | Alternatief 19 – Tekst | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Alternatief 19 - Waarde | Value for alternative 19 for Custom Menu 1 (CM1Alt19Value)
|  |  | Alternatief 20 – Tekst | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Alternatief 20 - Waarde | Value for alternative 20 for Custom Menu 1 (CM1Alt20Value)
|  |  | Alternatief 21 – Tekst | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Alternatief 21 - Waarde | Value for alternative 21 for Custom Menu 1 (CM1Alt21Value)
Aangepast menu 2
|  |  | Titel | Title for Custom Menu 2 (CM2Title)
|  |  | Actuele waarde | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Alternatief 1 - Tekst | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Alternatief 1 - Waarde | Value for alternative 1 for Custom Menu 2 (CM2Alt1Value)
|  |  | Alternatief 2 - Tekst | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Alternatief 2 - Waarde | Value for alternative 2 for Custom Menu 2 (CM2Alt2Value)
|  |  | Alternatief 3 - Tekst | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Alternatief 3 - Waarde | Value for alternative 3 for Custom Menu 2 (CM2Alt3Value)
|  |  | Alternatief 4 - Tekst | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Alternatief 4 - Waarde | Value for alternative 4 for Custom Menu 2 (CM2Alt4Value)
|  |  | Alternatief 5 - Tekst | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Alternatief 5 - Waarde | Value for alternative 5 for Custom Menu 2 (CM2Alt5Value)
|  |  | Alternatief 6 – Tekst | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Alternatief 6 - Waarde | Value for alternative 6 for Custom Menu 2 (CM2Alt6Value)
|  |  | Alternatief 7 – Tekst | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Alternatief 7 - Waarde | Value for alternative 7 for Custom Menu 2 (CM2Alt7Value)
|  |  | Alternatief 8 – Tekst | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Alternatief 8 - Waarde | Value for alternative 8 for Custom Menu 2 (CM2Alt8Value)
|  |  | Alternatief 9 – Tekst | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Alternatief 9 - Waarde | Value for alternative 9 for Custom Menu 2 (CM2Alt9Value)
|  |  | Alternatief 10 – Tekst | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Alternatief 10 – Waarde | Value for alternative 10 for Custom Menu 2 (CM2Alt10Value)
|  |  | Alternatief 11 – Tekst | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Alternatief 11 - Waarde | Value for alternative 11 for Custom Menu 2 (CM2Alt11Value)
|  |  | Alternatief 12 – Tekst | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Alternatief 12 - Waarde | Value for alternative 12 for Custom Menu 2 (CM2Alt12Value)
|  |  | Alternatief 13 – Tekst | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Alternatief 13 – Waarde | Value for alternative 13 for Custom Menu 2 (CM2Alt13Value)
|  |  | Alternatief 14 – Tekst | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Alternatief 14- Waarde | Value for alternative 14 for Custom Menu 2 (CM2Alt14Value)
|  |  | Alternatief 15 – Tekst | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Alternatief 15 – Waarde | Value for alternative 15 for Custom Menu 2 (CM2Alt15Value)
|  |  | Alternatief 16 – Tekst | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Alternatief 16 – Waarde | Value for alternative 16 for Custom Menu 2 (CM2Alt16Value)
|  |  | Alternatief 17 – Tekst | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Alternatief 17 – Waarde | Value for alternative 17 for Custom Menu 2 (CM2Alt17Value)
|  |  | Alternatief 18 – Tekst | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Alternatief 18 - Waarde | Value for alternative 18 for Custom Menu 2 (CM2Alt18Value)
|  |  | Alternatief 19 – Tekst | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Alternatief 19 - Waarde | Value for alternative 19 for Custom Menu 2 (CM2Alt19Value)
|  |  | Alternatief 20 – Tekst | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Alternatief 20 - Waarde | Value for alternative 20 for Custom Menu 2 (CM2Alt20Value)
|  |  | Alternatief 21 – Tekst | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Alternatief 21 - Waarde | Value for alternative 21 for Custom Menu 2 (CM2Alt21Value)
Aangepast menu 3
|  |  | Titel | Title for Custom Menu 3 (CM3Title)
|  |  | Actuele waarde | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Alternatief 1 - Tekst | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Alternatief 1 - Waarde | Value for alternative 1 for Custom Menu 3 (CM3Alt1Value)
|  |  | Alternatief 2 - Tekst | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Alternatief 2 - Waarde | Value for alternative 2 for Custom Menu 3 (CM3Alt2Value)
|  |  | Alternatief 3 - Tekst | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Alternatief 3 - Waarde | Value for alternative 3 for Custom Menu 3 (CM3Alt3Value)
|  |  | Alternatief 4 - Tekst | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Alternatief 4 - Waarde | Value for alternative 4 for Custom Menu 3 (CM3Alt4Value)
|  |  | Alternatief 5 - Tekst | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Alternatief 5 - Waarde | Value for alternative 5 for Custom Menu 3 (CM3Alt5Value)
|  |  | Alternatief 6 – Tekst | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Alternatief 6 - Waarde | Value for alternative 6 for Custom Menu 3 (CM3Alt6Value)
|  |  | Alternatief 7 – Tekst | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Alternatief 7 - Waarde | Value for alternative 7 for Custom Menu 3 (CM3Alt7Value)
|  |  | Alternatief 8 – Tekst | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Alternatief 8 - Waarde | Value for alternative 8 for Custom Menu 3 (CM3Alt8Value)
|  |  | Alternatief 9 – Tekst | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Alternatief 9 - Waarde | Value for alternative 9 for Custom Menu 3 (CM3Alt9Value)
|  |  | Alternatief 10 – Tekst | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Alternatief 10 – Waarde | Value for alternative 10 for Custom Menu 3 (CM3Alt10Value)
|  |  | Alternatief 11 – Tekst | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Alternatief 11 - Waarde | Value for alternative 11 for Custom Menu 3 (CM3Alt11Value)
|  |  | Alternatief 12 – Tekst | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Alternatief 12 - Waarde | Value for alternative 12 for Custom Menu 3 (CM3Alt12Value)
|  |  | Alternatief 13 – Tekst | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Alternatief 13 – Waarde | Value for alternative 13 for Custom Menu 3 (CM3Alt13Value)
|  |  | Alternatief 14 – Tekst | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Alternatief 14- Waarde | Value for alternative 14 for Custom Menu 3 (CM3Alt14Value)
|  |  | Alternatief 15 – Tekst | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Alternatief 15 – Waarde | Value for alternative 15 for Custom Menu 3 (CM3Alt15Value)
|  |  | Alternatief 16 – Tekst | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Alternatief 16 – Waarde | Value for alternative 16 for Custom Menu 3 (CM3Alt16Value)
|  |  | Alternatief 17 – Tekst | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Alternatief 17 – Waarde | Value for alternative 17 for Custom Menu 3 (CM3Alt17Value)
|  |  | Alternatief 18 – Tekst | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Alternatief 18 - Waarde | Value for alternative 18 for Custom Menu 3 (CM3Alt18Value)
|  |  | Alternatief 19 – Tekst | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Alternatief 19 - Waarde | Value for alternative 19 for Custom Menu 3 (CM3Alt19Value)
|  |  | Alternatief 20 – Tekst | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Alternatief 20 - Waarde | Value for alternative 20 for Custom Menu 3 (CM3Alt20Value)
|  |  | Alternatief 21 – Tekst | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Alternatief 21 - Waarde | Value for alternative 21 for Custom Menu 3 (CM3Alt21Value)
Aangepast menu 4
|  |  | Titel | Title for Custom Menu 4 (CM4Title)
|  |  | Actuele waarde | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Alternatief 1 - Tekst | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Alternatief 1 - Waarde | Value for alternative 1 for Custom Menu 4 (CM4Alt1Value)
|  |  | Alternatief 2 - Tekst | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Alternatief 2 - Waarde | Value for alternative 2 for Custom Menu 4 (CM4Alt2Value)
|  |  | Alternatief 3 - Tekst | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Alternatief 3 - Waarde | Value for alternative 3 for Custom Menu 4 (CM4Alt3Value)
|  |  | Alternatief 4 - Tekst | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Alternatief 4 - Waarde | Value for alternative 4 for Custom Menu 4 (CM4Alt4Value)
|  |  | Alternatief 5 - Tekst | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Alternatief 5 - Waarde | Value for alternative 5 for Custom Menu 4 (CM4Alt5Value)
|  |  | Alternatief 6 – Tekst | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Alternatief 6 - Waarde | Value for alternative 6 for Custom Menu 4 (CM4Alt6Value)
|  |  | Alternatief 7 – Tekst | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Alternatief 7 - Waarde | Value for alternative 7 for Custom Menu 4 (CM4Alt7Value)
|  |  | Alternatief 8 – Tekst | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Alternatief 8 - Waarde | Value for alternative 8 for Custom Menu 4 (CM4Alt8Value)
|  |  | Alternatief 9 – Tekst | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Alternatief 9 - Waarde | Value for alternative 9 for Custom Menu 4 (CM4Alt9Value)
|  |  | Alternatief 10 – Tekst | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Alternatief 10 – Waarde | Value for alternative 10 for Custom Menu 4 (CM4Alt10Value)
|  |  | Alternatief 11 – Tekst | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Alternatief 11 - Waarde | Value for alternative 11 for Custom Menu 4 (CM4Alt11Value)
|  |  | Alternatief 12 – Tekst | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Alternatief 12 - Waarde | Value for alternative 12 for Custom Menu 4 (CM4Alt12Value)
|  |  | Alternatief 13 – Tekst | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Alternatief 13 – Waarde | Value for alternative 13 for Custom Menu 4 (CM4Alt13Value)
|  |  | Alternatief 14 – Tekst | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Alternatief 14- Waarde | Value for alternative 14 for Custom Menu 4 (CM4Alt14Value)
|  |  | Alternatief 15 – Tekst | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Alternatief 15 – Waarde | Value for alternative 15 for Custom Menu 4 (CM4Alt15Value)
|  |  | Alternatief 16 – Tekst | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Alternatief 16 – Waarde | Value for alternative 16 for Custom Menu 4 (CM4Alt16Value)
|  |  | Alternatief 17 – Tekst | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Alternatief 17 – Waarde | Value for alternative 17 for Custom Menu 4 (CM4Alt17Value)
|  |  | Alternatief 18 – Tekst | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Alternatief 18 - Waarde | Value for alternative 18 for Custom Menu 4 (CM4Alt18Value)
|  |  | Alternatief 19 – Tekst | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Alternatief 19 - Waarde | Value for alternative 19 for Custom Menu 4 (CM4Alt19Value)
|  |  | Alternatief 20 – Tekst | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Alternatief 20 - Waarde | Value for alternative 20 for Custom Menu 4 (CM4Alt20Value)
|  |  | Alternatief 21 – Tekst | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Alternatief 21 - Waarde | Value for alternative 21 for Custom Menu 4 (CM4Alt21Value)
Aangepast menu 5
|  |  | Titel | Title for Custom Menu 5 (CM5Title)
|  |  | Actuele waarde | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Alternatief 1 - Tekst | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Alternatief 1 - Waarde | Value for alternative 1 for Custom Menu 5 (CM5Alt1Value)
|  |  | Alternatief 2 - Tekst | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Alternatief 2 - Waarde | Value for alternative 2 for Custom Menu 5 (CM5Alt2Value)
|  |  | Alternatief 3 - Tekst | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Alternatief 3 - Waarde | Value for alternative 3 for Custom Menu 5 (CM5Alt3Value)
|  |  | Alternatief 4 - Tekst | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Alternatief 4 - Waarde | Value for alternative 4 for Custom Menu 5 (CM5Alt4Value)
|  |  | Alternatief 5 - Tekst | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Alternatief 5 - Waarde | Value for alternative 5 for Custom Menu 5 (CM5Alt5Value)
|  |  | Alternatief 6 – Tekst | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Alternatief 6 - Waarde | Value for alternative 6 for Custom Menu 5 (CM5Alt6Value)
|  |  | Alternatief 7 – Tekst | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Alternatief 7 - Waarde | Value for alternative 7 for Custom Menu 5 (CM5Alt7Value)
|  |  | Alternatief 8 – Tekst | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Alternatief 8 - Waarde | Value for alternative 8 for Custom Menu 5 (CM5Alt8Value)
|  |  | Alternatief 9 – Tekst | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Alternatief 9 - Waarde | Value for alternative 9 for Custom Menu 5 (CM5Alt9Value)
|  |  | Alternatief 10 – Tekst | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Alternatief 10 – Waarde | Value for alternative 10 for Custom Menu 5 (CM5Alt10Value)
|  |  | Alternatief 11 – Tekst | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Alternatief 11 - Waarde | Value for alternative 11 for Custom Menu 5 (CM5Alt11Value)
|  |  | Alternatief 12 – Tekst | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Alternatief 12 - Waarde | Value for alternative 12 for Custom Menu 5 (CM5Alt12Value)
|  |  | Alternatief 13 – Tekst | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Alternatief 13 – Waarde | Value for alternative 13 for Custom Menu 5 (CM5Alt13Value)
|  |  | Alternatief 14 – Tekst | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Alternatief 14- Waarde | Value for alternative 14 for Custom Menu 5 (CM5Alt14Value)
|  |  | Alternatief 15 – Tekst | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Alternatief 15 – Waarde | Value for alternative 15 for Custom Menu 5 (CM5Alt15Value)
|  |  | Alternatief 16 – Tekst | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Alternatief 16 – Waarde | Value for alternative 16 for Custom Menu 5 (CM5Alt16Value)
|  |  | Alternatief 17 – Tekst | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Alternatief 17 – Waarde | Value for alternative 17 for Custom Menu 5 (CM5Alt17Value)
|  |  | Alternatief 18 – Tekst | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Alternatief 18 - Waarde | Value for alternative 18 for Custom Menu 5 (CM5Alt18Value)
|  |  | Alternatief 19 – Tekst | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Alternatief 19 - Waarde | Value for alternative 19 for Custom Menu 5 (CM5Alt19Value)
|  |  | Alternatief 20 – Tekst | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Alternatief 20 - Waarde | Value for alternative 20 for Custom Menu 5 (CM5Alt20Value)
|  |  | Alternatief 21 – Tekst | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Alternatief 21 - Waarde | Value for alternative 21 for Custom Menu 5 (CM5Alt21Value)
Aangepast menu 6
|  |  | Titel | Title for Custom Menu 6 (CM6Title)
|  |  | Actuele waarde | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Alternatief 1 - Tekst | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Alternatief 1 - Waarde | Value for alternative 1 for Custom Menu 6 (CM6Alt1Value)
|  |  | Alternatief 2 - Tekst | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Alternatief 2 - Waarde | Value for alternative 2 for Custom Menu 6 (CM6Alt2Value)
|  |  | Alternatief 3 - Tekst | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Alternatief 3 - Waarde | Value for alternative 3 for Custom Menu 6 (CM6Alt3Value)
|  |  | Alternatief 4 - Tekst | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Alternatief 4 - Waarde | Value for alternative 4 for Custom Menu 6 (CM6Alt4Value)
|  |  | Alternatief 5 - Tekst | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Alternatief 5 - Waarde | Value for alternative 5 for Custom Menu 6 (CM6Alt5Value)
|  |  | Alternatief 6 – Tekst | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Alternatief 6 - Waarde | Value for alternative 6 for Custom Menu 6 (CM6Alt6Value)
|  |  | Alternatief 7 – Tekst | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Alternatief 7 - Waarde | Value for alternative 7 for Custom Menu 6 (CM6Alt7Value)
|  |  | Alternatief 8 – Tekst | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Alternatief 8 - Waarde | Value for alternative 8 for Custom Menu 6 (CM6Alt8Value)
|  |  | Alternatief 9 – Tekst | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Alternatief 9 - Waarde | Value for alternative 9 for Custom Menu 6 (CM6Alt9Value)
|  |  | Alternatief 10 – Tekst | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Alternatief 10 – Waarde | Value for alternative 10 for Custom Menu 6 (CM6Alt10Value)
|  |  | Alternatief 11 – Tekst | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Alternatief 11 - Waarde | Value for alternative 11 for Custom Menu 6 (CM6Alt11Value)
|  |  | Alternatief 12 – Tekst | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Alternatief 12 - Waarde | Value for alternative 12 for Custom Menu 6 (CM6Alt12Value)
|  |  | Alternatief 13 – Tekst | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Alternatief 13 – Waarde | Value for alternative 13 for Custom Menu 6 (CM6Alt13Value)
|  |  | Alternatief 14 – Tekst | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternatief 14- Waarde | Value for alternative 14 for Custom Menu 6 (CM6Alt14Value)
|  |  | Alternatief 15 – Tekst | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Alternatief 15 – Waarde | Value for alternative 15 for Custom Menu 6 (CM6Alt15Value)
|  |  | Alternatief 16 – Tekst | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternatief 16 – Waarde | Value for alternative 16 for Custom Menu 6 (CM6Alt16Value)
|  |  | Alternatief 17 – Tekst | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Alternatief 17 – Waarde | Value for alternative 17 for Custom Menu 6 (CM6Alt17Value)
|  |  | Alternatief 18 – Tekst | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Alternatief 18 - Waarde | Value for alternative 18 for Custom Menu 6 (CM6Alt18Value)
|  |  | Alternatief 19 – Tekst | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Alternatief 19 - Waarde | Value for alternative 19 for Custom Menu 6 (CM6Alt19Value)
|  |  | Alternatief 20 – Tekst | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Alternatief 20 - Waarde | Value for alternative 20 for Custom Menu 6 (CM6Alt20Value)
|  |  | Alternatief 21 – Tekst | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Alternatief 21 - Waarde | Value for alternative 21 for Custom Menu 6 (CM6Alt21Value)
Aangepast menu 7
|  |  | Titel | Title for Custom Menu 7 (CM7Title)
|  |  | Actuele waarde | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Alternatief 1 - Tekst | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Alternatief 1 - Waarde | Value for alternative 1 for Custom Menu 7 (CM7Alt1Value)
|  |  | Alternatief 2 - Tekst | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Alternatief 2 - Waarde | Value for alternative 2 for Custom Menu 7 (CM7Alt2Value)
|  |  | Alternatief 3 - Tekst | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Alternatief 3 - Waarde | Value for alternative 3 for Custom Menu 7 (CM7Alt3Value)
|  |  | Alternatief 4 - Tekst | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Alternatief 4 - Waarde | Value for alternative 4 for Custom Menu 7 (CM7Alt4Value)
|  |  | Alternatief 5 - Tekst | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Alternatief 5 - Waarde | Value for alternative 5 for Custom Menu 7 (CM7Alt5Value)
|  |  | Alternatief 6 – Tekst | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Alternatief 6 - Waarde | Value for alternative 6 for Custom Menu 7 (CM7Alt6Value)
|  |  | Alternatief 7 – Tekst | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Alternatief 7 - Waarde | Value for alternative 7 for Custom Menu 7 (CM7Alt7Value)
|  |  | Alternatief 8 – Tekst | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Alternatief 8 - Waarde | Value for alternative 8 for Custom Menu 7 (CM7Alt8Value)
|  |  | Alternatief 9 – Tekst | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Alternatief 9 - Waarde | Value for alternative 9 for Custom Menu 7 (CM7Alt9Value)
|  |  | Alternatief 10 – Tekst | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Alternatief 10 – Waarde | Value for alternative 10 for Custom Menu 7 (CM7Alt10Value)
|  |  | Alternatief 11 – Tekst | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Alternatief 11 - Waarde | Value for alternative 11 for Custom Menu 7 (CM7Alt11Value)
|  |  | Alternatief 12 – Tekst | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Alternatief 12 - Waarde | Value for alternative 12 for Custom Menu 7 (CM7Alt12Value)
|  |  | Alternatief 13 – Tekst | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Alternatief 13 – Waarde | Value for alternative 13 for Custom Menu 7 (CM7Alt13Value)
|  |  | Alternatief 14 – Tekst | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Alternatief 14- Waarde | Value for alternative 14 for Custom Menu 7 (CM7Alt14Value)
|  |  | Alternatief 15 – Tekst | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Alternatief 15 – Waarde | Value for alternative 15 for Custom Menu 7 (CM7Alt15Value)
|  |  | Alternatief 16 – Tekst | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Alternatief 16 – Waarde | Value for alternative 16 for Custom Menu 7 (CM7Alt16Value)
|  |  | Alternatief 17 – Tekst | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Alternatief 17 – Waarde | Value for alternative 17 for Custom Menu 7 (CM7Alt17Value)
|  |  | Alternatief 18 – Tekst | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Alternatief 18 - Waarde | Value for alternative 18 for Custom Menu 7 (CM7Alt18Value)
|  |  | Alternatief 19 – Tekst | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Alternatief 19 - Waarde | Value for alternative 19 for Custom Menu 7 (CM7Alt19Value)
|  |  | Alternatief 20 – Tekst | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Alternatief 20 - Waarde | Value for alternative 20 for Custom Menu 7 (CM7Alt20Value)
|  |  | Alternatief 21 – Tekst | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Alternatief 21 - Waarde | Value for alternative 21 for Custom Menu 7 (CM7Alt21Value)
Aangepast menu 8
|  |  | Titel | Title for Custom Menu 8 (CM8Title)
|  |  | Actuele waarde | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Alternatief 1 - Tekst | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Alternatief 1 - Waarde | Value for alternative 1 for Custom Menu 8 (CM8Alt1Value)
|  |  | Alternatief 2 - Tekst | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Alternatief 2 - Waarde | Value for alternative 2 for Custom Menu 8 (CM8Alt2Value)
|  |  | Alternatief 3 - Tekst | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Alternatief 3 - Waarde | Value for alternative 3 for Custom Menu 8 (CM8Alt3Value)
|  |  | Alternatief 4 - Tekst | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Alternatief 4 - Waarde | Value for alternative 4 for Custom Menu 8 (CM8Alt4Value)
|  |  | Alternatief 5 - Tekst | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Alternatief 5 - Waarde | Value for alternative 5 for Custom Menu 8 (CM8Alt5Value)
|  |  | Alternatief 6 – Tekst | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Alternatief 6 - Waarde | Value for alternative 6 for Custom Menu 8 (CM8Alt6Value)
|  |  | Alternatief 7 – Tekst | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Alternatief 7 - Waarde | Value for alternative 7 for Custom Menu 8 (CM8Alt7Value)
|  |  | Alternatief 8 – Tekst | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Alternatief 8 - Waarde | Value for alternative 8 for Custom Menu 8 (CM8Alt8Value)
|  |  | Alternatief 9 – Tekst | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Alternatief 9 - Waarde | Value for alternative 9 for Custom Menu 8 (CM8Alt9Value)
|  |  | Alternatief 10 – Tekst | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Alternatief 10 – Waarde | Value for alternative 10 for Custom Menu 8 (CM8Alt10Value)
|  |  | Alternatief 11 – Tekst | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Alternatief 11 - Waarde | Value for alternative 11 for Custom Menu 8 (CM8Alt11Value)
|  |  | Alternatief 12 – Tekst | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Alternatief 12 - Waarde | Value for alternative 12 for Custom Menu 8 (CM8Alt12Value)
|  |  | Alternatief 13 – Tekst | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Alternatief 13 – Waarde | Value for alternative 13 for Custom Menu 8 (CM8Alt13Value)
|  |  | Alternatief 14 – Tekst | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Alternatief 14- Waarde | Value for alternative 14 for Custom Menu 8 (CM8Alt14Value)
|  |  | Alternatief 15 – Tekst | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Alternatief 15 – Waarde | Value for alternative 15 for Custom Menu 8 (CM8Alt15Value)
|  |  | Alternatief 16 – Tekst | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Alternatief 16 – Waarde | Value for alternative 16 for Custom Menu 8 (CM8Alt16Value)
|  |  | Alternatief 17 – Tekst | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Alternatief 17 – Waarde | Value for alternative 17 for Custom Menu 8 (CM8Alt17Value)
|  |  | Alternatief 18 – Tekst | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Alternatief 18 - Waarde | Value for alternative 18 for Custom Menu 8 (CM8Alt18Value)
|  |  | Alternatief 19 – Tekst | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Alternatief 19 - Waarde | Value for alternative 19 for Custom Menu 8 (CM8Alt19Value)
|  |  | Alternatief 20 – Tekst | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Alternatief 20 - Waarde | Value for alternative 20 for Custom Menu 8 (CM8Alt20Value)
|  |  | Alternatief 21 – Tekst | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Alternatief 21 - Waarde | Value for alternative 21 for Custom Menu 8 (CM8Alt21Value)
Servomotoren
Aan/uit-uitgangen
|  |  | Verwarmingshysterese, ruimte temperatuur [ºC] | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Koelhysterese, ruimte temperatuur [ºC] | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysterese, extra zone temperatuur [ºC] | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Kleppentest
|  |  | Kleppentest | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Interval verwarmen [h] | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Interval verwarmen 2 [h] | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Interval koelen [h] | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Interval koelen 2 [h] | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Interval change-over [h] | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | Interval 6-wegklep [h] | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Duur verwarming [s] | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Duur verwarming 2 [s] | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Duur koeling [s] | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Duur koeling 2 [s] | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Duur change-over [s] | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | Duur 6-wegklep [s] | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analoge ingangen
Temperatuur ingang
|  |  | Filtertijd [s] | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperatuur ingang 0-10V
|  |  | Waarde bij 0 V [°C] | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Waarde bij 10 V [°C] | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2 ingang
|  |  | Waarde bij 0 V [ppm] | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Waarde bij 10 V [ppm] | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filtertijd [s] | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Vochtigheid ingang
|  |  | Waarde bij 0 V [%] | RH at 0 Volt input (RC_RH_0V)
|  |  | Waarde bij 10 V [%] | RH at 10 Volt input (RC_RH_10V)
|  |  | Filtertijd [s] | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Flow ingang
|  |  | Waarde bij 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Waarde bij 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filtertijd [s] | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC ingang
|  |  | Waarde bij 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Waarde bij 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filtertijd [s] | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Gewenste waarden
Ruimte gewenst
|  |  | Verwarming, aanwezig [°C] | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Koeling, aanwezig [°C] | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Verwarming, stand-by [°C] | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Koeling, stand-by [°C] | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Verwarming, afwezig [°C] | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Koeling, afwezig [°C] | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Vorst beveiliging [°C] | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Gewenste verstelling
|  |  | Max gewenste verstelling omhoog [°C] | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Max gewenste verstelling omlaag [°C] | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Gewenste verstelling [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Extra zone
|  |  | Extra zone gewenst [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2 gewenst [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Vochtigheid
|  |  | Vochtigheid gewenst [%] | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC gewenst | Setpoint for VOC control (RC_VOCSetpoint)
PI-regelaars
Ruimte
|  |  | P-band [°C] | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-tijd [s] | I-time for room PID controller (RC_RoomPIDItime)
Inblaas regeling
|  |  | Regeling actief | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Versterkingsfactor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Max. verwarmingstemperatuur [°C] | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min. verwarmingstemperatuur [°C] | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Max. koeltemperatuur [°C] | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min. koeltemperatuur [°C] | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Vorst beveiliging temperatuur [°C] | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Extra zone
|  |  | P-band [°C] | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-tijd [s] | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-band [ppm] | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-tijd [s] | I-time for CO2 PID controller (RC_CO2PIDItime)
Vochtigheid
|  |  | P-band [%] | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-tijd [s] | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-band | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-tijd [s] | I-time for VOC PID controller (RC_VOCPIDItime)
Alarm instellingen
Alarm ruimte temperatuur
|  |  | Bovengrenswaarde [°C] | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Ondergrenswaarde [°C] | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
Alarm CO2-niveau
|  |  | Bovengrenswaarde [ppm] | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Invoer aanpassingen
UI1
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_2_offset)
Ruimte temperatuur
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_5_offset)
Ruimte vochtigheid
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_6_offset)
VOC sensor
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_7_offset)
CO2 sensor
|  |  | Grenswaarden modus | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Offset aanpassing | Offset for input (IoAnaIn_8_offset)
Uitgang instellingen
UO1
|  |  | Minimumwaarde | Scale for output (IoAnaOut_1_min_in)
|  |  | Maximumwaarde | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maximumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_1_max_out)
|  |  | Offset op basis van volledig bereik [-100=-100%, 100=100%] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Minimumwaarde | Scale for output (IoAnaOut_2_min_in)
|  |  | Maximumwaarde | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maximumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_2_max_out)
|  |  | Offset op basis van volledig bereik [-100=-100%, 100=100%] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Minimumwaarde | Scale for output (IoAnaOut_3_min_in)
|  |  | Maximumwaarde | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maximumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_3_max_out)
|  |  | Offset op basis van volledig bereik [-100=-100%, 100=100%] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Minimumwaarde | Scale for output (IoAnaOut_4_min_in)
|  |  | Maximumwaarde | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maximumwaarde [0=0%, 100=100%] | Scale for output (IoAnaOut_4_max_out)
|  |  | Offset op basis van volledig bereik [-100=-100%, 100=100%] | Offset for output (IoAnaOut_4_offset)
Handmatig/Auto
Externe waarden
Ruimte temperatuur
|  |  | Hand sturing | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Gewenst [°C] | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Ruimte temperatuur [°C] | Room temperature (RC_RoomTemp)
Inblaas temperatuur
|  |  | Hand sturing | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Gewenst [°C] | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Inblaas temperatuur [°C] | Supply air temperature (RC_SupplyAirTemp)
Extra zone temperatuur
|  |  | Hand sturing | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Gewenst [°C] | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Extra zone temperatuur [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
Change-over temperatuur
|  |  | Hand sturing | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Gewenst [°C] | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-over temperatuur [°C] | Changeover temperature (RC_ChangeOverTemp)
Change-over VAV temperatuur
|  |  | Hand sturing | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Gewenst [°C] | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-over VAV temperatuur [°C] | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2 niveau
|  |  | Hand sturing | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Gewenst [ppm] | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2 niveau [ppm] | Room CO2 level (RC_CO2Level)
Ruimte vochtigheid
|  |  | Hand sturing | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Gewenst [%] | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Ruimte vochtigheid [%] | Relative humidity (RC_Humidity)
Lucht Flow
|  |  | Hand sturing | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Gewenst | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Lucht Flow | Air flow (RC_AirFlow)
VOC-index
|  |  | Hand sturing | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Gewenst | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC-index | VOC index (RC_VOC)
Aanwezigheid detector
|  |  | Hand sturing | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Gewenst | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Aanwezigheid detector | Presence indication (RC_Presence)
Open raam
|  |  | Hand sturing | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Gewenst | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Open raam | Open window indication (RC_DIOpenWindow)
Condensatie
|  |  | Hand sturing | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Gewenst | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Condensatie | Condensation indication (RC_DICondensation)
Extern alarm (DI)
|  |  | Hand sturing | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Gewenst | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | Extern alarm (DI) | Digital input alarm (RC_AlarmDI)
Change-over DI
|  |  | Hand sturing | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Gewenst | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-over DI | Change-over digital input (RC_DIChangeOver)
Change-over VAV DI
|  |  | Hand sturing | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Gewenst | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-over VAV DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Handmatig/Auto
Regelaar status
|  |  | Regelaar status | Current state (RC_ControllerState)
|  |  | GBS overschrijven | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Uitschakelen | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Geforceerde ventilatie | Set controller in Bypass state (RC_ControllerStateSetBypass)
Ventilator regeling
|  |  | Ventilator regeling | Fan speed setting (RC_FanSelect)
Verwarming uitgang
|  |  | Modus | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Gewenst [%] | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Verwarming uitgang [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Modus | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Verwarming uitgang | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Verwarming 2 uitgang
|  |  | Modus | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Gewenst [%] | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Verwarming 2 uitgang [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Modus | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Verwarming 2 uitgang | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Koeling uitgang
|  |  | Modus | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Gewenst [%] | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Koeling uitgang [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Modus | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Koeling uitgang | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Koeling 2 uitgang
|  |  | Modus | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Gewenst [%] | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Koeling 2 uitgang [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Modus | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Koeling 2 uitgang | Room control Cool2 output digital (RC_RoomCool2OutputDO)
VAV uitgang
|  |  | Modus | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Gewenst [%] | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | VAV uitgang [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
VAV 2 uitgang
|  |  | Modus | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Gewenst [%] | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | VAV 2 uitgang [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Change-over uitgang
|  |  | Modus | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Gewenst [%] | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Change-over uitgang [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Change-over VAV uitgang
|  |  | Modus | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Gewenst [%] | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Change-over VAV uitgang [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
6-wegklep uitgang
|  |  | Modus | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Modus | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Gewenst [%] | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | 6-wegklep uitgang [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Extra zone uitgang
|  |  | Modus | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Gewenst [%] | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Extra zone uitgang | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC Ventilator regeling
|  |  | Modus | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Gewenst [%] | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC Ventilator regeling [%] | Current EC fan speed (RC_ECFanSpeed)
CO2-regeling uitgang
|  |  | Modus | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Gewenst [%] | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | CO2-regeling uitgang [%] | CO2 control analog out (RC_CO2ControlAO)
Vochtigheidsregeling uitgang
|  |  | Modus | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Gewenst [%] | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Vochtigheidsregeling uitgang [%] | Humidify analog out (RC_HumidifyOutputAO)
Ontvochtigingsregeling uitgang
|  |  | Modus | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Gewenst [%] | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Ontvochtigingsregeling uitgang [%] | Dehumidify analog out (RC_DehumidifyOutputAO)
VOC-regeling uitgang
|  |  | Modus | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Gewenst [%] | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | VOC-regeling uitgang [%] | VOC control analog out (RC_VOCControlAO)
Extra zone actief uitgang
|  |  | Modus | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Extra zone actief uitgang | Extra Zone active (RC_ExtraZoneActive)
Geforceerde ventilatie uitgang
|  |  | Modus | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Geforceerde ventilatie uitgang | Forced ventilation output (RC_ForcedVentDO)
Hardware regeling
UO1
|  |  | UO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Modus | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Ingestelde waarde [0=0%, 100=100%] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Modus | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Gewenst | Override value (IoDo_1_override)
UO2
|  |  | UO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Modus | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Ingestelde waarde [0=0%, 100=100%] | Override value (IoAnaOut_2_override)
|  |  | UO2: | Value set for output (IoDo_2_value)
|  |  | Modus | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Gewenst | Override value (IoDo_2_override)
AO1
|  |  | AO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Modus | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Ingestelde waarde [0=0%, 100=100%] | Override value (IoAnaOut_3_override)
AO2
|  |  | AO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Modus | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Ingestelde waarde [0=0%, 100=100%] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Modus | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Gewenst | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Modus | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Gewenst | Override value (IoAnaIn_2_override)
Kalibratie CO2-sensor
|  |  | Automatische zelfkalibratie inschakelen | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Uitgangspunt automatische zelfkalibratie [ppm] [ppm] | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | Voer geforceerde herkalibratie van CO2-sensor uit | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | CO2-referentieniveau voor geforceerde herkalibratie [ppm] [ppm] | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Laatste geforceerde herkalibratie-offset (-9999 = Fout) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | Reset CO2-sensor | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Relais uitgang
|  |  | Relais status | Value set for output (IoDo_3_value)
|  |  | Modus | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Gewenst | Override value (IoDo_3_override)
PIR sensor
|  |  | PIR sensor | Filtered value from sensor (IoDiIn_4_value)
|  |  | Modus | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Gewenst | Override value (IoDiIn_4_override)
Apparaat
Apparaat-ID
Apparaat-ID
|  |  | Naam | (ControllerName)
|  |  | Omschrijving | Controller description (ControllerDescription)
|  |  | Locatie | Controller location (ControllerLocation)
|  |  | Project | (ControllerProject)
Communicatie
Poortinstellingen
|  |  | Poort 1 functie | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Poort 1 baudrate | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Poort 1 pariteit | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbus adres | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | BACnet MSTP adres | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | MSTP max master adres | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet apparaat ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet apparaat objectnaam | BACnet device object name (BACnetDeviceObjectName)
|  |  | Wachtwoord | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth-functie | Function for BLE button (BleButtonMode)
|  |  | Uitschakeling na [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | BLE zendvermogen | BLE TX power level (ble_power)
Communicatiestoring
|  |  | Foutactie | Offline function (RC_OfflineFunction)
|  |  | Time-out [s] | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Fallback status | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Reset
Reset
|  |  | Herstart regelaar | Write to this register will trigger resets with different reset reasons (product_reset)
Niet-vluchtig geheugen
Niet-vluchtig geheugen
|  |  | Niet-vluchtig geheugen uitschakelen | Set to 1 to disable storage in non volatile memory (disable_nv_storage)

## sv
RCX-2.1-1-01 - Menu Structure |  |  |  | Revision: B
Tab | Menu | Group | Item | Description
Dashboard
Översikt
System
|  |  | Regulator | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbusadress | Active Modbus unit ID (ModbusUnitID)
|  |  | MSTP-adress för BACnet | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet enhets-ID | BACnet device ID (BACnetDeviceID)
|  |  | Summalarm | Sum Alarm (RC_SumAlarm)
Rum
|  |  | Regulatorläge | Current state (RC_ControllerState)
|  |  | Driftläge | Current controller mode (RC_ControllerMode)
|  |  | Rumstemperatur [°C] | Room temperature (RC_RoomTemp)
|  |  | Tilluftstemperatur [°C] | Supply air temperature (RC_SupplyAirTemp)
|  |  | Rumsbörvärde [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Börvärdesjustering [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC-fläkthastighet [%] | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2-nivå [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Luftfuktighet i rum [%] | Relative humidity (RC_Humidity)
|  |  | VOC-index | VOC index (RC_VOC)
|  |  | Närvarostyrning | Presence indication (RC_Presence)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Extra zon
|  |  | Extra zon, temperatur [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Extra zon, börvärde [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Aktiv utgång för extra zon | Extra Zone active (RC_ExtraZoneActive)
Ärvärden
Rumsstyrningssekvens
|  |  | Sekvens 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sekvens 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sekvens 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Ärvärden
|  |  | Driftläge | Current controller mode (RC_ControllerMode)
|  |  | Rumstemperatur [°C] | Room temperature (RC_RoomTemp)
|  |  | Rumsbörvärde [°C] | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Börvärdesjustering [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Värmebehov [%] | Room PID heat output (RC_PIDHeatDemand)
|  |  | Kylbehov [%] | Room PID cool output (RC_PIDCoolDemand)
|  |  | Värme-utgång [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Värme 2-utgång [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Kyla-utgång [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Kyla 2-utgång [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | VAV-utgång [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | VAV 2-utgång [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-over-temperatur | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-over-läge | Change-over status (RC_ChangeOverState)
|  |  | Change-over-utgång [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-over VAV-temperatur | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-over VAV-läge | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | VAV-utgång för change-over [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | Utgång för 6-vägsventil [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2-nivå [ppm] | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2-börvärde [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Reläutgång
|  |  | Relästatus | Value set for output (IoDo_3_value)
Ingångar/Utgångar
Universella ingångar
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universella utgångar
|  |  | UO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analoga utgångar
|  |  | AO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Interna givare
|  |  | Rumstemperatur [°C] | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2-givare [ppm] | Filtered value from sensor (IoAnaIn_8_value)
|  |  | Fuktgivare [%] | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC-givare | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR-givare | Filtered value from sensor (IoDiIn_4_value)
Larm
Larm
|  |  | Summalarm | Sum Alarm (RC_SumAlarm)
|  |  | Givarfel | Sensor error alarm (RC_AlarmSensorError)
|  |  | Hög rumstemperatur | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Låg rumstemperatur | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | Hög CO2-nivå | High CO2 alarm (RC_AlarmCO2High)
|  |  | Externt larm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Utgång i manuellt läge | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Felkod för temperaturgivare | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Felkod för fuktighetsgivare | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | Felkod för VOC-givare | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | Felkod för CO2-givare | Detailed fault description (IoAnaIn_8_errorFlags)
Om
Enhets-ID
|  |  | Serienummer | (SerialNumberString)
|  |  | Namn | (ControllerName)
|  |  | Beskrivning | Controller description (ControllerDescription)
|  |  | Plats | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Anpassade menyer
Anpassad meny 1
|  |  | Titel | Title for Custom Menu 1 (CM1Title)
|  |  | Nuvarande värde | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Nuvarande alternativ | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Nuvarande alternativ | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Nuvarande alternativ | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Nuvarande alternativ | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Nuvarande alternativ | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Nuvarande alternativ | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Nuvarande alternativ | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Nuvarande alternativ | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Nuvarande alternativ | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Nuvarande alternativ | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Nuvarande alternativ | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Nuvarande alternativ | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Nuvarande alternativ | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Nuvarande alternativ | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Nuvarande alternativ | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Nuvarande alternativ | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Nuvarande alternativ | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Nuvarande alternativ | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Nuvarande alternativ | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Nuvarande alternativ | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Nuvarande alternativ | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Aktuellt alternativindex | Current alternative for Custom Menu 1 (CM1CurrentAlt)
Anpassad meny 2
|  |  | Titel | Title for Custom Menu 2 (CM2Title)
|  |  | Nuvarande värde | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Nuvarande alternativ | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Nuvarande alternativ | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Nuvarande alternativ | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Nuvarande alternativ | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Nuvarande alternativ | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Nuvarande alternativ | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Nuvarande alternativ | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Nuvarande alternativ | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Nuvarande alternativ | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Nuvarande alternativ | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Nuvarande alternativ | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Nuvarande alternativ | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Nuvarande alternativ | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Nuvarande alternativ | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Nuvarande alternativ | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Nuvarande alternativ | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Nuvarande alternativ | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Nuvarande alternativ | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Nuvarande alternativ | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Nuvarande alternativ | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Nuvarande alternativ | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Aktuellt alternativindex | Current alternative for Custom Menu 2 (CM2CurrentAlt)
Anpassad meny 3
|  |  | Titel | Title for Custom Menu 3 (CM3Title)
|  |  | Nuvarande värde | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Nuvarande alternativ | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Nuvarande alternativ | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Nuvarande alternativ | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Nuvarande alternativ | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Nuvarande alternativ | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Nuvarande alternativ | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Nuvarande alternativ | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Nuvarande alternativ | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Nuvarande alternativ | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Nuvarande alternativ | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Nuvarande alternativ | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Nuvarande alternativ | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Nuvarande alternativ | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Nuvarande alternativ | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Nuvarande alternativ | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Nuvarande alternativ | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Nuvarande alternativ | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Nuvarande alternativ | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Nuvarande alternativ | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Nuvarande alternativ | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Nuvarande alternativ | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Aktuellt alternativindex | Current alternative for Custom Menu 3 (CM3CurrentAlt)
Anpassad meny 4
|  |  | Titel | Title for Custom Menu 4 (CM4Title)
|  |  | Nuvarande värde | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Nuvarande alternativ | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Nuvarande alternativ | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Nuvarande alternativ | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Nuvarande alternativ | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Nuvarande alternativ | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Nuvarande alternativ | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Nuvarande alternativ | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Nuvarande alternativ | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Nuvarande alternativ | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Nuvarande alternativ | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Nuvarande alternativ | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Nuvarande alternativ | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Nuvarande alternativ | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Nuvarande alternativ | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Nuvarande alternativ | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Nuvarande alternativ | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Nuvarande alternativ | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Nuvarande alternativ | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Nuvarande alternativ | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Nuvarande alternativ | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Nuvarande alternativ | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Aktuellt alternativindex | Current alternative for Custom Menu 4 (CM4CurrentAlt)
Anpassad meny 5
|  |  | Titel | Title for Custom Menu 5 (CM5Title)
|  |  | Nuvarande värde | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Nuvarande alternativ | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Nuvarande alternativ | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Nuvarande alternativ | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Nuvarande alternativ | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Nuvarande alternativ | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Nuvarande alternativ | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Nuvarande alternativ | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Nuvarande alternativ | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Nuvarande alternativ | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Nuvarande alternativ | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Nuvarande alternativ | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Nuvarande alternativ | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Nuvarande alternativ | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Nuvarande alternativ | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Nuvarande alternativ | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Nuvarande alternativ | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Nuvarande alternativ | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Nuvarande alternativ | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Nuvarande alternativ | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Nuvarande alternativ | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Nuvarande alternativ | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Aktuellt alternativindex | Current alternative for Custom Menu 5 (CM5CurrentAlt)
Anpassad meny 6
|  |  | Titel | Title for Custom Menu 6 (CM6Title)
|  |  | Nuvarande värde | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Nuvarande alternativ | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Nuvarande alternativ | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Nuvarande alternativ | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Nuvarande alternativ | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Nuvarande alternativ | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Nuvarande alternativ | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Nuvarande alternativ | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Nuvarande alternativ | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Nuvarande alternativ | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Nuvarande alternativ | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Nuvarande alternativ | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Nuvarande alternativ | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Nuvarande alternativ | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Nuvarande alternativ | Text for alternative 14 for Custom Menu 6 (CM6Alt14Text)
|  |  | Nuvarande alternativ | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Nuvarande alternativ | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Nuvarande alternativ | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Nuvarande alternativ | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Nuvarande alternativ | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Nuvarande alternativ | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Nuvarande alternativ | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Aktuellt alternativindex | Current alternative for Custom Menu 6 (CM6CurrentAlt)
Anpassad meny 7
|  |  | Titel | Title for Custom Menu 7 (CM7Title)
|  |  | Nuvarande värde | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Nuvarande alternativ | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Nuvarande alternativ | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Nuvarande alternativ | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Nuvarande alternativ | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Nuvarande alternativ | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Nuvarande alternativ | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Nuvarande alternativ | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Nuvarande alternativ | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Nuvarande alternativ | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Nuvarande alternativ | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Nuvarande alternativ | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Nuvarande alternativ | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Nuvarande alternativ | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Nuvarande alternativ | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Nuvarande alternativ | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Nuvarande alternativ | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Nuvarande alternativ | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Nuvarande alternativ | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Nuvarande alternativ | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Nuvarande alternativ | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Nuvarande alternativ | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Aktuellt alternativindex | Current alternative for Custom Menu 7 (CM7CurrentAlt)
Anpassad meny 8
|  |  | Titel | Title for Custom Menu 8 (CM8Title)
|  |  | Nuvarande värde | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Nuvarande alternativ | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Nuvarande alternativ | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Nuvarande alternativ | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Nuvarande alternativ | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Nuvarande alternativ | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Nuvarande alternativ | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Nuvarande alternativ | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Nuvarande alternativ | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Nuvarande alternativ | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Nuvarande alternativ | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Nuvarande alternativ | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Nuvarande alternativ | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Nuvarande alternativ | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Nuvarande alternativ | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Nuvarande alternativ | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Nuvarande alternativ | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Nuvarande alternativ | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Nuvarande alternativ | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Nuvarande alternativ | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Nuvarande alternativ | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Nuvarande alternativ | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Aktuellt alternativindex | Current alternative for Custom Menu 8 (CM8CurrentAlt)
Konfigurering
Reglerfunktioner
Rumsstyrningssekvens
|  |  | Sekvens 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sekvens 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sekvens 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Värme
|  |  | Max.gräns [%] | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min.gräns [%] | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Fläkt av, fördröjning för elvärme | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Följ change-over-läge | Heat1 included in change-over function (RC_Heat1InChangeOver)
Värme 2
|  |  | Max.gräns [%] | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min.gräns [%] | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Fläkt av, fördröjning för elvärme | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Följ change-over-läge | Heat2 included in change-over function (RC_Heat2InChangeOver)
Kyla
|  |  | Max.gräns [%] | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min.gräns [%] | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Ställ in på max. vid forcerad ventilation | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Stäng av utgång när fläkten är avstängd | Turn off Cool1 output when the fan is off (RC_Cool1OffWhenFanIsOff)
|  |  | Följ change-over-läge | Cool1 included in change-over function (RC_Cool1InChangeOver)
Kyla 2
|  |  | Max.gräns [%] | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min.gräns [%] | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Ställ in på max. vid forcerad ventilation | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Stäng av utgång när fläkten är avstängd | Turn off Cool2 output when the fan is off (RC_Cool2OffWhenFanIsOff)
|  |  | Följ change-over-läge | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Max.gräns [%] | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min.gräns, av [%] | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min.gräns, unoccupied [%] | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min.gräns, standby [%] | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min.gräns, Närvaro [%] | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min.gräns, forcerad ventilation [%] | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Ställ in på max. vid forcerad ventilation | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Maxgräns vid värme [%] | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Följ change-over-läge | VAV1 included in change-over function (RC_VAV1InChangeOver)
|  |  | Starta VAV när föregående kylsekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Starta VAV när föregående värmesekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VAV 2
|  |  | Max.gräns [%] | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min.gräns, av [%] | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min.gräns, unoccupied [%] | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min.gräns, standby [%] | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min.gräns, Närvaro [%] | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min.gräns, forcerad ventilation [%] | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Ställ in på max. vid forcerad ventilation | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Maxgräns vid värme [%] | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Följ change-over-läge | VAV2 included in change-over function (RC_VAV2InChangeOver)
|  |  | Starta VAV när föregående kylsekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Starta VAV när föregående värmesekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
VAV-reglering källa
|  |  | Kylbehov | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2-nivå | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC-index | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Luftfuktighet | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Max.gräns [%] | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min.gräns [%] | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Driftläge | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-over-temperatur [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Värmehysteres [°C] | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Kylhysteres [°C] | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Ventil, fördröjningstid [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over-VAV
|  |  | Max.gräns [%] | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min.gräns, av [%] | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min.gräns, unoccupied [%] | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min.gräns, standby [%] | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min.gräns, Närvaro [%] | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min.gräns, forcerad ventilation [%] | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Ställ in på max. vid forcerad ventilation | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Driftläge | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-over-temperatur [°C] | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Värmehysteres [°C] | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Kylhysteres [°C] | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Ventil, fördröjningstid [s] | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
|  |  | Starta VAV när föregående kylsekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartCool)
|  |  | Starta VAV när föregående värmesekvens når [%] | Start VAV sequence when previous output reaches this value (RC_VAVSequenceStartHeat)
6-vägsventil
|  |  | Sekv. 1 helt öppen [V] | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Sekv. 1 börja öppna [V] | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Sekv. 2 helt öppen [V] | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Sekv. 2 börja öppna [V] | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Mittpunkt [V] | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Hysteres för mittpunkt [%] | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Sekvensordning | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Följ change-over-läge | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Regulatorläge
|  |  | Förinställt läge | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Shutdown-läge | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Öppet fönster-läge | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Tid i forcerat ventilationsläge [min] | Bypass time (minutes) (RC_BypassTime)
Forcerad ventilation
|  |  | Aktiv när | Forced ventilation function (RC_ForcedVentMode)
|  |  | Startgräns [%] | Forced ventilation start limit (RC_ForcedVentStartLimit)
Närvarostyrning
|  |  | Närvaroläge | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Aktiv fördröjning [min] | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Inaktiv fördröjning [min] | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2-aktivering | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2-nivå [ppm] | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2-hysteres [ppm] | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Använd intern PIR för närvaro | Use internal PIR sensor for presence detection (RC_PIRPresence)
Extra zon
Extra zon
|  |  | Funktion för extra zon | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Inaktiverad under läge | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Inaktivera om huvudzonläge skiljer sig från funktion | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min.gräns [%] | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Max.gräns [%] | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Ingångar/Utgångar
Universella ingångar
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universella utgångar
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | UO1 tidsperiod för termisk ventil [s] | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | UO1 styrsignal | Unit converter (IoAnaOut_1_unit)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | UO2 tidsperiod för termoventil [s] | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
|  |  | UO2 styrsignal | Unit converter (IoAnaOut_2_unit)
Analoga utgångar
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO1 styrsignal | Unit converter (IoAnaOut_3_unit)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
|  |  | AO2 styrsignal | Unit converter (IoAnaOut_4_unit)
Fläktstyrning
Fläktregleringskälla
|  |  | Rumsregulator | Select fan control mode (RC_FanControlMode)
|  |  | CO2-nivå | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Luftfuktighet | Fan is controlled by humidity output (RC_FanControlHumidity)
EC-fläktreglering
|  |  | Hastighet vid inget behov | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Av vid under behov [%] | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysteres för minskning av fläkthastigheten [%] | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Starthastighet [%] | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Max. hastighet i autoläge [%] | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Hastighet för forcerad ventilation | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Hastighet för forcerad ventilation [%] | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Hastighet 1 utgång [%] | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Hastighet 2 utgång [%] | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Hastighet 3 utgång [%] | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Mögelskydd | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Fläkt, kickstart
|  |  | Tid för kick-start [s] | Fan kick start time (RC_FanKickStartTime)
Fläkt, frånslagsfördröjning
|  |  | Av-tidsfördröjning [s] | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Min. hastighet | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Fläkt, boost
|  |  | Driftläge | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Tid för boostning [s] | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-band | Fan boost P band (RC_FanBoostPBand)
Display och menyer
Display
|  |  | Startskärm | What to display during device startup (DisplayStartupMode)
|  |  | Visningsläge | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Börvärdesläge | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | Avrunda CO2-värdet till närmaste | Min step for CO2 value (RC_CO2Step)
|  |  | Full ljusstyrka [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Dim timeout, 0 = Alltid full [s] | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Dimmad ljusstyrka [%] | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Av-timeout, 0 = Aldrig av [s] | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Viloläge display
|  |  | Temperatur/börvärde | Show temperature/setpoint in idle view (App_IdleViewTemperature)
|  |  | CO2-nivå | Show CO2 value in idle view (App_IdleViewCO2)
|  |  | Luftfuktighet i rum | Show humidity in idle view (App_IdleViewHumidity)
|  |  | VOC-index | Show VOC in idle view (App_IdleViewVOC)
|  |  | Regulatorläge | Show mode in idle view (App_IdleViewMode)
Meny
|  |  | Sida för börvärdesjustering | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Menysida driftläge | Enable Mode menu page (App_EnableMenuMode)
|  |  | Menysida för change-over | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Menysida för fläkt | Enable Fan menu page (App_EnableMenuFan)
|  |  | Menysida för forcerad ventilation | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Förlängd drift för forcerad ventilation | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Sida för temperatur/börvärde | Enable Temperature menu page (App_EnableMenuTemp)
|  |  | Menysida för luftfuktighet | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | Menysida för CO2 | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | Menysida för VOC | Enable VOC menu page (App_EnableMenuVOC)
Displayordning
|  |  | Displayposition 1 | Display position 1 (DisplayPosition1)
|  |  | Displayposition 2 | Display position 2 (DisplayPosition2)
|  |  | Displayposition 3 | Display position 3 (DisplayPosition3)
|  |  | Displayposition 4 | Display position 4 (DisplayPosition4)
|  |  | Displayposition 5 | Display position 5 (DisplayPosition5)
|  |  | Displayposition 6 | Display position 6 (DisplayPosition6)
|  |  | Displayposition 7 | Display position 7 (DisplayPosition7)
|  |  | Displayposition 8 | Display position 8 (DisplayPosition8)
|  |  | Displayposition 9 | Display position 9 (DisplayPosition9)
|  |  | Displayposition 10 | Display position 10 (DisplayPosition10)
|  |  | Displayposition 11 | Display position 11 (DisplayPosition11)
|  |  | Displayposition 12 | Display position 12 (DisplayPosition12)
Anpassade menyval
|  |  | Anpassad meny 1 | Enable Custom Menu 1 (CM1Enabled)
|  |  | Anpassad meny 2 | Enable Custom Menu 2 (CM2Enabled)
|  |  | Anpassad meny 3 | Enable Custom Menu 3 (CM3Enabled)
|  |  | Anpassad meny 4 | Enable Custom Menu 4 (CM4Enabled)
|  |  | Anpassad meny 5 | Enable Custom Menu 5 (CM5Enabled)
|  |  | Anpassad meny 6 | Enable Custom Menu 6 (CM6Enabled)
|  |  | Anpassad meny 7 | Enable Custom Menu 7 (CM7Enabled)
|  |  | Anpassad meny 8 | Enable Custom Menu 8 (CM8Enabled)
Alternativ i driftslägesmenyn
|  |  | Text för menyrubrik | Mode menu title (App_ModeMenuTitle)
|  |  | Aktivera driftläget Av | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Aktivera driftläget Ej Närvaro | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Aktivera driftläget Standby | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Aktivera driftläget Närvaro | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Aktivera driftläget Forcerad ventilation | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Text för driftläget Av | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Text för driftläget Ej Närvaro | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Text för driftläget Standby | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Text för driftläget Närvaro | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Text för driftläget Forcerad ventilation | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Text för driftläget Auto | Mode menu Auto state text (App_ModeMenuAutoText)
Alternativ i change-over-menyn
|  |  | Text för menyrubrik | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | Aktivera driftläget Värme | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | Aktivera läget Kyla | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | Aktivera läget Auto | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | Text för läget Värme | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | Text för läget Kyla | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | Text för läget Auto | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
LED-indikering
|  |  | Ljusstyrka [%] | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 LED-indikering | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Gul LED CO2-nivå [ppm] | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Röd LED CO2-nivå [ppm] | CO2 level for red led (RC_CO2LevelRed)
Anpassade texter
|  |  | Visningsläge | When to show the custom text (rt_text_visability)
|  |  | Displayläge | Single or dual row text in display (rt_text_mode)
|  |  | Bläddringsläge | Scroll mode (rt_text_display_scroll_mode)
|  |  | Teckensnitt | What font to use for the display text (rt_text_font)
|  |  | Bläddring, fördröjning [ms] | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Timervärde för anpassad text [s] | Time to show the custom text (rt_text_timeleft)
|  |  | Anpassad text rad 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Anpassad text rad 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Anpassad text 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Anpassad text 2 | String to show on row 2 in the display (rt_text_row_2)
Anpassade menyer
Anpassad meny 1
|  |  | Titel | Title for Custom Menu 1 (CM1Title)
|  |  | Nuvarande värde | Current value for Custom Menu 1 (CM1CurrentValue)
|  |  | Alternativ 1 – Text | Text for alternative 1 for Custom Menu 1 (CM1Alt1Text)
|  |  | Alternativ 1 – Värde | Value for alternative 1 for Custom Menu 1 (CM1Alt1Value)
|  |  | Alternativ 2 – Text | Text for alternative 2 for Custom Menu 1 (CM1Alt2Text)
|  |  | Alternativ 2 – Värde | Value for alternative 2 for Custom Menu 1 (CM1Alt2Value)
|  |  | Alternativ 3 – Text | Text for alternative 3 for Custom Menu 1 (CM1Alt3Text)
|  |  | Alternativ 3 – Värde | Value for alternative 3 for Custom Menu 1 (CM1Alt3Value)
|  |  | Alternativ 4 – Text | Text for alternative 4 for Custom Menu 1 (CM1Alt4Text)
|  |  | Alternativ 4 – Värde | Value for alternative 4 for Custom Menu 1 (CM1Alt4Value)
|  |  | Alternativ 5 – Text | Text for alternative 5 for Custom Menu 1 (CM1Alt5Text)
|  |  | Alternativ 5 – Värde | Value for alternative 5 for Custom Menu 1 (CM1Alt5Value)
|  |  | Alternativ 6 – Text | Text for alternative 6 for Custom Menu 1 (CM1Alt6Text)
|  |  | Alternativ 6 – Värde | Value for alternative 6 for Custom Menu 1 (CM1Alt6Value)
|  |  | Alternativ 7 – Text | Text for alternative 7 for Custom Menu 1 (CM1Alt7Text)
|  |  | Alternativ 7 – Värde | Value for alternative 7 for Custom Menu 1 (CM1Alt7Value)
|  |  | Alternativ 8 – Text | Text for alternative 8 for Custom Menu 1 (CM1Alt8Text)
|  |  | Alternativ 8 – Värde | Value for alternative 8 for Custom Menu 1 (CM1Alt8Value)
|  |  | Alternativ 9 – Text | Text for alternative 9 for Custom Menu 1 (CM1Alt9Text)
|  |  | Alternativ 9 – Värde | Value for alternative 9 for Custom Menu 1 (CM1Alt9Value)
|  |  | Alternativ 10 – Text | Text for alternative 10 for Custom Menu 1 (CM1Alt10Text)
|  |  | Alternativ 10 – Värde | Value for alternative 10 for Custom Menu 1 (CM1Alt10Value)
|  |  | Alternativ 11 – Text | Text for alternative 11 for Custom Menu 1 (CM1Alt11Text)
|  |  | Alternativ 11 – Värde | Value for alternative 11 for Custom Menu 1 (CM1Alt11Value)
|  |  | Alternativ 12 – Text | Text for alternative 12 for Custom Menu 1 (CM1Alt12Text)
|  |  | Alternativ 12 – Värde | Value for alternative 12 for Custom Menu 1 (CM1Alt12Value)
|  |  | Alternativ 13 – Text | Text for alternative 13 for Custom Menu 1 (CM1Alt13Text)
|  |  | Alternativ 13 – Värde | Value for alternative 13 for Custom Menu 1 (CM1Alt13Value)
|  |  | Alternativ 14 – Text | Text for alternative 14 for Custom Menu 1 (CM1Alt14Text)
|  |  | Alternativ 14 – Värde | Value for alternative 14 for Custom Menu 1 (CM1Alt14Value)
|  |  | Alternativ 15 – Text | Text for alternative 15 for Custom Menu 1 (CM1Alt15Text)
|  |  | Alternativ 15 – Värde | Value for alternative 15 for Custom Menu 1 (CM1Alt15Value)
|  |  | Alternativ 16 – Text | Text for alternative 16 for Custom Menu 1 (CM1Alt16Text)
|  |  | Alternativ 16 – Värde | Value for alternative 16 for Custom Menu 1 (CM1Alt16Value)
|  |  | Alternativ 17 – Text | Text for alternative 17 for Custom Menu 1 (CM1Alt17Text)
|  |  | Alternativ 17 – Värde | Value for alternative 17 for Custom Menu 1 (CM1Alt17Value)
|  |  | Alternativ 18 – Text | Text for alternative 18 for Custom Menu 1 (CM1Alt18Text)
|  |  | Alternativ 18 – Värde | Value for alternative 18 for Custom Menu 1 (CM1Alt18Value)
|  |  | Alternativ 19 – Text | Text for alternative 19 for Custom Menu 1 (CM1Alt19Text)
|  |  | Alternativ 19 – Värde | Value for alternative 19 for Custom Menu 1 (CM1Alt19Value)
|  |  | Alternativ 20 – Text | Text for alternative 20 for Custom Menu 1 (CM1Alt20Text)
|  |  | Alternativ 20 – Värde | Value for alternative 20 for Custom Menu 1 (CM1Alt20Value)
|  |  | Alternativ 21 – Text | Text for alternative 21 for Custom Menu 1 (CM1Alt21Text)
|  |  | Alternativ 21 - Värde | Value for alternative 21 for Custom Menu 1 (CM1Alt21Value)
Anpassad meny 2
|  |  | Titel | Title for Custom Menu 2 (CM2Title)
|  |  | Nuvarande värde | Current value for Custom Menu 2 (CM2CurrentValue)
|  |  | Alternativ 1 – Text | Text for alternative 1 for Custom Menu 2 (CM2Alt1Text)
|  |  | Alternativ 1 – Värde | Value for alternative 1 for Custom Menu 2 (CM2Alt1Value)
|  |  | Alternativ 2 – Text | Text for alternative 2 for Custom Menu 2 (CM2Alt2Text)
|  |  | Alternativ 2 – Värde | Value for alternative 2 for Custom Menu 2 (CM2Alt2Value)
|  |  | Alternativ 3 – Text | Text for alternative 3 for Custom Menu 2 (CM2Alt3Text)
|  |  | Alternativ 3 – Värde | Value for alternative 3 for Custom Menu 2 (CM2Alt3Value)
|  |  | Alternativ 4 – Text | Text for alternative 4 for Custom Menu 2 (CM2Alt4Text)
|  |  | Alternativ 4 – Värde | Value for alternative 4 for Custom Menu 2 (CM2Alt4Value)
|  |  | Alternativ 5 – Text | Text for alternative 5 for Custom Menu 2 (CM2Alt5Text)
|  |  | Alternativ 5 – Värde | Value for alternative 5 for Custom Menu 2 (CM2Alt5Value)
|  |  | Alternativ 6 – Text | Text for alternative 6 for Custom Menu 2 (CM2Alt6Text)
|  |  | Alternativ 6 – Värde | Value for alternative 6 for Custom Menu 2 (CM2Alt6Value)
|  |  | Alternativ 7 – Text | Text for alternative 7 for Custom Menu 2 (CM2Alt7Text)
|  |  | Alternativ 7 – Värde | Value for alternative 7 for Custom Menu 2 (CM2Alt7Value)
|  |  | Alternativ 8 – Text | Text for alternative 8 for Custom Menu 2 (CM2Alt8Text)
|  |  | Alternativ 8 – Värde | Value for alternative 8 for Custom Menu 2 (CM2Alt8Value)
|  |  | Alternativ 9 – Text | Text for alternative 9 for Custom Menu 2 (CM2Alt9Text)
|  |  | Alternativ 9 – Värde | Value for alternative 9 for Custom Menu 2 (CM2Alt9Value)
|  |  | Alternativ 10 – Text | Text for alternative 10 for Custom Menu 2 (CM2Alt10Text)
|  |  | Alternativ 10 – Värde | Value for alternative 10 for Custom Menu 2 (CM2Alt10Value)
|  |  | Alternativ 11 – Text | Text for alternative 11 for Custom Menu 2 (CM2Alt11Text)
|  |  | Alternativ 11 – Värde | Value for alternative 11 for Custom Menu 2 (CM2Alt11Value)
|  |  | Alternativ 12 – Text | Text for alternative 12 for Custom Menu 2 (CM2Alt12Text)
|  |  | Alternativ 12 – Värde | Value for alternative 12 for Custom Menu 2 (CM2Alt12Value)
|  |  | Alternativ 13 – Text | Text for alternative 13 for Custom Menu 2 (CM2Alt13Text)
|  |  | Alternativ 13 – Värde | Value for alternative 13 for Custom Menu 2 (CM2Alt13Value)
|  |  | Alternativ 14 – Text | Text for alternative 14 for Custom Menu 2 (CM2Alt14Text)
|  |  | Alternativ 14 – Värde | Value for alternative 14 for Custom Menu 2 (CM2Alt14Value)
|  |  | Alternativ 15 – Text | Text for alternative 15 for Custom Menu 2 (CM2Alt15Text)
|  |  | Alternativ 15 – Värde | Value for alternative 15 for Custom Menu 2 (CM2Alt15Value)
|  |  | Alternativ 16 – Text | Text for alternative 16 for Custom Menu 2 (CM2Alt16Text)
|  |  | Alternativ 16 – Värde | Value for alternative 16 for Custom Menu 2 (CM2Alt16Value)
|  |  | Alternativ 17 – Text | Text for alternative 17 for Custom Menu 2 (CM2Alt17Text)
|  |  | Alternativ 17 – Värde | Value for alternative 17 for Custom Menu 2 (CM2Alt17Value)
|  |  | Alternativ 18 – Text | Text for alternative 18 for Custom Menu 2 (CM2Alt18Text)
|  |  | Alternativ 18 – Värde | Value for alternative 18 for Custom Menu 2 (CM2Alt18Value)
|  |  | Alternativ 19 – Text | Text for alternative 19 for Custom Menu 2 (CM2Alt19Text)
|  |  | Alternativ 19 – Värde | Value for alternative 19 for Custom Menu 2 (CM2Alt19Value)
|  |  | Alternativ 20 – Text | Text for alternative 20 for Custom Menu 2 (CM2Alt20Text)
|  |  | Alternativ 20 – Värde | Value for alternative 20 for Custom Menu 2 (CM2Alt20Value)
|  |  | Alternativ 21 – Text | Text for alternative 21 for Custom Menu 2 (CM2Alt21Text)
|  |  | Alternativ 21 - Värde | Value for alternative 21 for Custom Menu 2 (CM2Alt21Value)
Anpassad meny 3
|  |  | Titel | Title for Custom Menu 3 (CM3Title)
|  |  | Nuvarande värde | Current value for Custom Menu 3 (CM3CurrentValue)
|  |  | Alternativ 1 – Text | Text for alternative 1 for Custom Menu 3 (CM3Alt1Text)
|  |  | Alternativ 1 – Värde | Value for alternative 1 for Custom Menu 3 (CM3Alt1Value)
|  |  | Alternativ 2 – Text | Text for alternative 2 for Custom Menu 3 (CM3Alt2Text)
|  |  | Alternativ 2 – Värde | Value for alternative 2 for Custom Menu 3 (CM3Alt2Value)
|  |  | Alternativ 3 – Text | Text for alternative 3 for Custom Menu 3 (CM3Alt3Text)
|  |  | Alternativ 3 – Värde | Value for alternative 3 for Custom Menu 3 (CM3Alt3Value)
|  |  | Alternativ 4 – Text | Text for alternative 4 for Custom Menu 3 (CM3Alt4Text)
|  |  | Alternativ 4 – Värde | Value for alternative 4 for Custom Menu 3 (CM3Alt4Value)
|  |  | Alternativ 5 – Text | Text for alternative 5 for Custom Menu 3 (CM3Alt5Text)
|  |  | Alternativ 5 – Värde | Value for alternative 5 for Custom Menu 3 (CM3Alt5Value)
|  |  | Alternativ 6 – Text | Text for alternative 6 for Custom Menu 3 (CM3Alt6Text)
|  |  | Alternativ 6 – Värde | Value for alternative 6 for Custom Menu 3 (CM3Alt6Value)
|  |  | Alternativ 7 – Text | Text for alternative 7 for Custom Menu 3 (CM3Alt7Text)
|  |  | Alternativ 7 – Värde | Value for alternative 7 for Custom Menu 3 (CM3Alt7Value)
|  |  | Alternativ 8 – Text | Text for alternative 8 for Custom Menu 3 (CM3Alt8Text)
|  |  | Alternativ 8 – Värde | Value for alternative 8 for Custom Menu 3 (CM3Alt8Value)
|  |  | Alternativ 9 – Text | Text for alternative 9 for Custom Menu 3 (CM3Alt9Text)
|  |  | Alternativ 9 – Värde | Value for alternative 9 for Custom Menu 3 (CM3Alt9Value)
|  |  | Alternativ 10 – Text | Text for alternative 10 for Custom Menu 3 (CM3Alt10Text)
|  |  | Alternativ 10 – Värde | Value for alternative 10 for Custom Menu 3 (CM3Alt10Value)
|  |  | Alternativ 11 – Text | Text for alternative 11 for Custom Menu 3 (CM3Alt11Text)
|  |  | Alternativ 11 – Värde | Value for alternative 11 for Custom Menu 3 (CM3Alt11Value)
|  |  | Alternativ 12 – Text | Text for alternative 12 for Custom Menu 3 (CM3Alt12Text)
|  |  | Alternativ 12 – Värde | Value for alternative 12 for Custom Menu 3 (CM3Alt12Value)
|  |  | Alternativ 13 – Text | Text for alternative 13 for Custom Menu 3 (CM3Alt13Text)
|  |  | Alternativ 13 – Värde | Value for alternative 13 for Custom Menu 3 (CM3Alt13Value)
|  |  | Alternativ 14 – Text | Text for alternative 14 for Custom Menu 3 (CM3Alt14Text)
|  |  | Alternativ 14 – Värde | Value for alternative 14 for Custom Menu 3 (CM3Alt14Value)
|  |  | Alternativ 15 – Text | Text for alternative 15 for Custom Menu 3 (CM3Alt15Text)
|  |  | Alternativ 15 – Värde | Value for alternative 15 for Custom Menu 3 (CM3Alt15Value)
|  |  | Alternativ 16 – Text | Text for alternative 16 for Custom Menu 3 (CM3Alt16Text)
|  |  | Alternativ 16 – Värde | Value for alternative 16 for Custom Menu 3 (CM3Alt16Value)
|  |  | Alternativ 17 – Text | Text for alternative 17 for Custom Menu 3 (CM3Alt17Text)
|  |  | Alternativ 17 – Värde | Value for alternative 17 for Custom Menu 3 (CM3Alt17Value)
|  |  | Alternativ 18 – Text | Text for alternative 18 for Custom Menu 3 (CM3Alt18Text)
|  |  | Alternativ 18 – Värde | Value for alternative 18 for Custom Menu 3 (CM3Alt18Value)
|  |  | Alternativ 19 – Text | Text for alternative 19 for Custom Menu 3 (CM3Alt19Text)
|  |  | Alternativ 19 – Värde | Value for alternative 19 for Custom Menu 3 (CM3Alt19Value)
|  |  | Alternativ 20 – Text | Text for alternative 20 for Custom Menu 3 (CM3Alt20Text)
|  |  | Alternativ 20 – Värde | Value for alternative 20 for Custom Menu 3 (CM3Alt20Value)
|  |  | Alternativ 21 – Text | Text for alternative 21 for Custom Menu 3 (CM3Alt21Text)
|  |  | Alternativ 21 - Värde | Value for alternative 21 for Custom Menu 3 (CM3Alt21Value)
Anpassad meny 4
|  |  | Titel | Title for Custom Menu 4 (CM4Title)
|  |  | Nuvarande värde | Current value for Custom Menu 4 (CM4CurrentValue)
|  |  | Alternativ 1 – Text | Text for alternative 1 for Custom Menu 4 (CM4Alt1Text)
|  |  | Alternativ 1 – Värde | Value for alternative 1 for Custom Menu 4 (CM4Alt1Value)
|  |  | Alternativ 2 – Text | Text for alternative 2 for Custom Menu 4 (CM4Alt2Text)
|  |  | Alternativ 2 – Värde | Value for alternative 2 for Custom Menu 4 (CM4Alt2Value)
|  |  | Alternativ 3 – Text | Text for alternative 3 for Custom Menu 4 (CM4Alt3Text)
|  |  | Alternativ 3 – Värde | Value for alternative 3 for Custom Menu 4 (CM4Alt3Value)
|  |  | Alternativ 4 – Text | Text for alternative 4 for Custom Menu 4 (CM4Alt4Text)
|  |  | Alternativ 4 – Värde | Value for alternative 4 for Custom Menu 4 (CM4Alt4Value)
|  |  | Alternativ 5 – Text | Text for alternative 5 for Custom Menu 4 (CM4Alt5Text)
|  |  | Alternativ 5 – Värde | Value for alternative 5 for Custom Menu 4 (CM4Alt5Value)
|  |  | Alternativ 6 – Text | Text for alternative 6 for Custom Menu 4 (CM4Alt6Text)
|  |  | Alternativ 6 – Värde | Value for alternative 6 for Custom Menu 4 (CM4Alt6Value)
|  |  | Alternativ 7 – Text | Text for alternative 7 for Custom Menu 4 (CM4Alt7Text)
|  |  | Alternativ 7 – Värde | Value for alternative 7 for Custom Menu 4 (CM4Alt7Value)
|  |  | Alternativ 8 – Text | Text for alternative 8 for Custom Menu 4 (CM4Alt8Text)
|  |  | Alternativ 8 – Värde | Value for alternative 8 for Custom Menu 4 (CM4Alt8Value)
|  |  | Alternativ 9 – Text | Text for alternative 9 for Custom Menu 4 (CM4Alt9Text)
|  |  | Alternativ 9 – Värde | Value for alternative 9 for Custom Menu 4 (CM4Alt9Value)
|  |  | Alternativ 10 – Text | Text for alternative 10 for Custom Menu 4 (CM4Alt10Text)
|  |  | Alternativ 10 – Värde | Value for alternative 10 for Custom Menu 4 (CM4Alt10Value)
|  |  | Alternativ 11 – Text | Text for alternative 11 for Custom Menu 4 (CM4Alt11Text)
|  |  | Alternativ 11 – Värde | Value for alternative 11 for Custom Menu 4 (CM4Alt11Value)
|  |  | Alternativ 12 – Text | Text for alternative 12 for Custom Menu 4 (CM4Alt12Text)
|  |  | Alternativ 12 – Värde | Value for alternative 12 for Custom Menu 4 (CM4Alt12Value)
|  |  | Alternativ 13 – Text | Text for alternative 13 for Custom Menu 4 (CM4Alt13Text)
|  |  | Alternativ 13 – Värde | Value for alternative 13 for Custom Menu 4 (CM4Alt13Value)
|  |  | Alternativ 14 – Text | Text for alternative 14 for Custom Menu 4 (CM4Alt14Text)
|  |  | Alternativ 14 – Värde | Value for alternative 14 for Custom Menu 4 (CM4Alt14Value)
|  |  | Alternativ 15 – Text | Text for alternative 15 for Custom Menu 4 (CM4Alt15Text)
|  |  | Alternativ 15 – Värde | Value for alternative 15 for Custom Menu 4 (CM4Alt15Value)
|  |  | Alternativ 16 – Text | Text for alternative 16 for Custom Menu 4 (CM4Alt16Text)
|  |  | Alternativ 16 – Värde | Value for alternative 16 for Custom Menu 4 (CM4Alt16Value)
|  |  | Alternativ 17 – Text | Text for alternative 17 for Custom Menu 4 (CM4Alt17Text)
|  |  | Alternativ 17 – Värde | Value for alternative 17 for Custom Menu 4 (CM4Alt17Value)
|  |  | Alternativ 18 – Text | Text for alternative 18 for Custom Menu 4 (CM4Alt18Text)
|  |  | Alternativ 18 – Värde | Value for alternative 18 for Custom Menu 4 (CM4Alt18Value)
|  |  | Alternativ 19 – Text | Text for alternative 19 for Custom Menu 4 (CM4Alt19Text)
|  |  | Alternativ 19 – Värde | Value for alternative 19 for Custom Menu 4 (CM4Alt19Value)
|  |  | Alternativ 20 – Text | Text for alternative 20 for Custom Menu 4 (CM4Alt20Text)
|  |  | Alternativ 20 – Värde | Value for alternative 20 for Custom Menu 4 (CM4Alt20Value)
|  |  | Alternativ 21 – Text | Text for alternative 21 for Custom Menu 4 (CM4Alt21Text)
|  |  | Alternativ 21 - Värde | Value for alternative 21 for Custom Menu 4 (CM4Alt21Value)
Anpassad meny 5
|  |  | Titel | Title for Custom Menu 5 (CM5Title)
|  |  | Nuvarande värde | Current value for Custom Menu 5 (CM5CurrentValue)
|  |  | Alternativ 1 – Text | Text for alternative 1 for Custom Menu 5 (CM5Alt1Text)
|  |  | Alternativ 1 – Värde | Value for alternative 1 for Custom Menu 5 (CM5Alt1Value)
|  |  | Alternativ 2 – Text | Text for alternative 2 for Custom Menu 5 (CM5Alt2Text)
|  |  | Alternativ 2 – Värde | Value for alternative 2 for Custom Menu 5 (CM5Alt2Value)
|  |  | Alternativ 3 – Text | Text for alternative 3 for Custom Menu 5 (CM5Alt3Text)
|  |  | Alternativ 3 – Värde | Value for alternative 3 for Custom Menu 5 (CM5Alt3Value)
|  |  | Alternativ 4 – Text | Text for alternative 4 for Custom Menu 5 (CM5Alt4Text)
|  |  | Alternativ 4 – Värde | Value for alternative 4 for Custom Menu 5 (CM5Alt4Value)
|  |  | Alternativ 5 – Text | Text for alternative 5 for Custom Menu 5 (CM5Alt5Text)
|  |  | Alternativ 5 – Värde | Value for alternative 5 for Custom Menu 5 (CM5Alt5Value)
|  |  | Alternativ 6 – Text | Text for alternative 6 for Custom Menu 5 (CM5Alt6Text)
|  |  | Alternativ 6 – Värde | Value for alternative 6 for Custom Menu 5 (CM5Alt6Value)
|  |  | Alternativ 7 – Text | Text for alternative 7 for Custom Menu 5 (CM5Alt7Text)
|  |  | Alternativ 7 – Värde | Value for alternative 7 for Custom Menu 5 (CM5Alt7Value)
|  |  | Alternativ 8 – Text | Text for alternative 8 for Custom Menu 5 (CM5Alt8Text)
|  |  | Alternativ 8 – Värde | Value for alternative 8 for Custom Menu 5 (CM5Alt8Value)
|  |  | Alternativ 9 – Text | Text for alternative 9 for Custom Menu 5 (CM5Alt9Text)
|  |  | Alternativ 9 – Värde | Value for alternative 9 for Custom Menu 5 (CM5Alt9Value)
|  |  | Alternativ 10 – Text | Text for alternative 10 for Custom Menu 5 (CM5Alt10Text)
|  |  | Alternativ 10 – Värde | Value for alternative 10 for Custom Menu 5 (CM5Alt10Value)
|  |  | Alternativ 11 – Text | Text for alternative 11 for Custom Menu 5 (CM5Alt11Text)
|  |  | Alternativ 11 – Värde | Value for alternative 11 for Custom Menu 5 (CM5Alt11Value)
|  |  | Alternativ 12 – Text | Text for alternative 12 for Custom Menu 5 (CM5Alt12Text)
|  |  | Alternativ 12 – Värde | Value for alternative 12 for Custom Menu 5 (CM5Alt12Value)
|  |  | Alternativ 13 – Text | Text for alternative 13 for Custom Menu 5 (CM5Alt13Text)
|  |  | Alternativ 13 – Värde | Value for alternative 13 for Custom Menu 5 (CM5Alt13Value)
|  |  | Alternativ 14 – Text | Text for alternative 14 for Custom Menu 5 (CM5Alt14Text)
|  |  | Alternativ 14 – Värde | Value for alternative 14 for Custom Menu 5 (CM5Alt14Value)
|  |  | Alternativ 15 – Text | Text for alternative 15 for Custom Menu 5 (CM5Alt15Text)
|  |  | Alternativ 15 – Värde | Value for alternative 15 for Custom Menu 5 (CM5Alt15Value)
|  |  | Alternativ 16 – Text | Text for alternative 16 for Custom Menu 5 (CM5Alt16Text)
|  |  | Alternativ 16 – Värde | Value for alternative 16 for Custom Menu 5 (CM5Alt16Value)
|  |  | Alternativ 17 – Text | Text for alternative 17 for Custom Menu 5 (CM5Alt17Text)
|  |  | Alternativ 17 – Värde | Value for alternative 17 for Custom Menu 5 (CM5Alt17Value)
|  |  | Alternativ 18 – Text | Text for alternative 18 for Custom Menu 5 (CM5Alt18Text)
|  |  | Alternativ 18 – Värde | Value for alternative 18 for Custom Menu 5 (CM5Alt18Value)
|  |  | Alternativ 19 – Text | Text for alternative 19 for Custom Menu 5 (CM5Alt19Text)
|  |  | Alternativ 19 – Värde | Value for alternative 19 for Custom Menu 5 (CM5Alt19Value)
|  |  | Alternativ 20 – Text | Text for alternative 20 for Custom Menu 5 (CM5Alt20Text)
|  |  | Alternativ 20 – Värde | Value for alternative 20 for Custom Menu 5 (CM5Alt20Value)
|  |  | Alternativ 21 – Text | Text for alternative 21 for Custom Menu 5 (CM5Alt21Text)
|  |  | Alternativ 21 - Värde | Value for alternative 21 for Custom Menu 5 (CM5Alt21Value)
Anpassad meny 6
|  |  | Titel | Title for Custom Menu 6 (CM6Title)
|  |  | Nuvarande värde | Current value for Custom Menu 6 (CM6CurrentValue)
|  |  | Alternativ 1 – Text | Text for alternative 1 for Custom Menu 6 (CM6Alt1Text)
|  |  | Alternativ 1 – Värde | Value for alternative 1 for Custom Menu 6 (CM6Alt1Value)
|  |  | Alternativ 2 – Text | Text for alternative 2 for Custom Menu 6 (CM6Alt2Text)
|  |  | Alternativ 2 – Värde | Value for alternative 2 for Custom Menu 6 (CM6Alt2Value)
|  |  | Alternativ 3 – Text | Text for alternative 3 for Custom Menu 6 (CM6Alt3Text)
|  |  | Alternativ 3 – Värde | Value for alternative 3 for Custom Menu 6 (CM6Alt3Value)
|  |  | Alternativ 4 – Text | Text for alternative 4 for Custom Menu 6 (CM6Alt4Text)
|  |  | Alternativ 4 – Värde | Value for alternative 4 for Custom Menu 6 (CM6Alt4Value)
|  |  | Alternativ 5 – Text | Text for alternative 5 for Custom Menu 6 (CM6Alt5Text)
|  |  | Alternativ 5 – Värde | Value for alternative 5 for Custom Menu 6 (CM6Alt5Value)
|  |  | Alternativ 6 – Text | Text for alternative 6 for Custom Menu 6 (CM6Alt6Text)
|  |  | Alternativ 6 – Värde | Value for alternative 6 for Custom Menu 6 (CM6Alt6Value)
|  |  | Alternativ 7 – Text | Text for alternative 7 for Custom Menu 6 (CM6Alt7Text)
|  |  | Alternativ 7 – Värde | Value for alternative 7 for Custom Menu 6 (CM6Alt7Value)
|  |  | Alternativ 8 – Text | Text for alternative 8 for Custom Menu 6 (CM6Alt8Text)
|  |  | Alternativ 8 – Värde | Value for alternative 8 for Custom Menu 6 (CM6Alt8Value)
|  |  | Alternativ 9 – Text | Text for alternative 9 for Custom Menu 6 (CM6Alt9Text)
|  |  | Alternativ 9 – Värde | Value for alternative 9 for Custom Menu 6 (CM6Alt9Value)
|  |  | Alternativ 10 – Text | Text for alternative 10 for Custom Menu 6 (CM6Alt10Text)
|  |  | Alternativ 10 – Värde | Value for alternative 10 for Custom Menu 6 (CM6Alt10Value)
|  |  | Alternativ 11 – Text | Text for alternative 11 for Custom Menu 6 (CM6Alt11Text)
|  |  | Alternativ 11 – Värde | Value for alternative 11 for Custom Menu 6 (CM6Alt11Value)
|  |  | Alternativ 12 – Text | Text for alternative 12 for Custom Menu 6 (CM6Alt12Text)
|  |  | Alternativ 12 – Värde | Value for alternative 12 for Custom Menu 6 (CM6Alt12Value)
|  |  | Alternativ 13 – Text | Text for alternative 13 for Custom Menu 6 (CM6Alt13Text)
|  |  | Alternativ 13 – Värde | Value for alternative 13 for Custom Menu 6 (CM6Alt13Value)
|  |  | Alternativ 14 – Text | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternativ 14 – Värde | Value for alternative 14 for Custom Menu 6 (CM6Alt14Value)
|  |  | Alternativ 15 – Text | Text for alternative 15 for Custom Menu 6 (CM6Alt15Text)
|  |  | Alternativ 15 – Värde | Value for alternative 15 for Custom Menu 6 (CM6Alt15Value)
|  |  | Alternativ 16 – Text | Text for alternative 16 for Custom Menu 6 (CM6Alt16Text)
|  |  | Alternativ 16 – Värde | Value for alternative 16 for Custom Menu 6 (CM6Alt16Value)
|  |  | Alternativ 17 – Text | Text for alternative 17 for Custom Menu 6 (CM6Alt17Text)
|  |  | Alternativ 17 – Värde | Value for alternative 17 for Custom Menu 6 (CM6Alt17Value)
|  |  | Alternativ 18 – Text | Text for alternative 18 for Custom Menu 6 (CM6Alt18Text)
|  |  | Alternativ 18 – Värde | Value for alternative 18 for Custom Menu 6 (CM6Alt18Value)
|  |  | Alternativ 19 – Text | Text for alternative 19 for Custom Menu 6 (CM6Alt19Text)
|  |  | Alternativ 19 – Värde | Value for alternative 19 for Custom Menu 6 (CM6Alt19Value)
|  |  | Alternativ 20 – Text | Text for alternative 20 for Custom Menu 6 (CM6Alt20Text)
|  |  | Alternativ 20 – Värde | Value for alternative 20 for Custom Menu 6 (CM6Alt20Value)
|  |  | Alternativ 21 – Text | Text for alternative 21 for Custom Menu 6 (CM6Alt21Text)
|  |  | Alternativ 21 - Värde | Value for alternative 21 for Custom Menu 6 (CM6Alt21Value)
Anpassad meny 7
|  |  | Titel | Title for Custom Menu 7 (CM7Title)
|  |  | Nuvarande värde | Current value for Custom Menu 7 (CM7CurrentValue)
|  |  | Alternativ 1 – Text | Text for alternative 1 for Custom Menu 7 (CM7Alt1Text)
|  |  | Alternativ 1 – Värde | Value for alternative 1 for Custom Menu 7 (CM7Alt1Value)
|  |  | Alternativ 2 – Text | Text for alternative 2 for Custom Menu 7 (CM7Alt2Text)
|  |  | Alternativ 2 – Värde | Value for alternative 2 for Custom Menu 7 (CM7Alt2Value)
|  |  | Alternativ 3 – Text | Text for alternative 3 for Custom Menu 7 (CM7Alt3Text)
|  |  | Alternativ 3 – Värde | Value for alternative 3 for Custom Menu 7 (CM7Alt3Value)
|  |  | Alternativ 4 – Text | Text for alternative 4 for Custom Menu 7 (CM7Alt4Text)
|  |  | Alternativ 4 – Värde | Value for alternative 4 for Custom Menu 7 (CM7Alt4Value)
|  |  | Alternativ 5 – Text | Text for alternative 5 for Custom Menu 7 (CM7Alt5Text)
|  |  | Alternativ 5 – Värde | Value for alternative 5 for Custom Menu 7 (CM7Alt5Value)
|  |  | Alternativ 6 – Text | Text for alternative 6 for Custom Menu 7 (CM7Alt6Text)
|  |  | Alternativ 6 – Värde | Value for alternative 6 for Custom Menu 7 (CM7Alt6Value)
|  |  | Alternativ 7 – Text | Text for alternative 7 for Custom Menu 7 (CM7Alt7Text)
|  |  | Alternativ 7 – Värde | Value for alternative 7 for Custom Menu 7 (CM7Alt7Value)
|  |  | Alternativ 8 – Text | Text for alternative 8 for Custom Menu 7 (CM7Alt8Text)
|  |  | Alternativ 8 – Värde | Value for alternative 8 for Custom Menu 7 (CM7Alt8Value)
|  |  | Alternativ 9 – Text | Text for alternative 9 for Custom Menu 7 (CM7Alt9Text)
|  |  | Alternativ 9 – Värde | Value for alternative 9 for Custom Menu 7 (CM7Alt9Value)
|  |  | Alternativ 10 – Text | Text for alternative 10 for Custom Menu 7 (CM7Alt10Text)
|  |  | Alternativ 10 – Värde | Value for alternative 10 for Custom Menu 7 (CM7Alt10Value)
|  |  | Alternativ 11 – Text | Text for alternative 11 for Custom Menu 7 (CM7Alt11Text)
|  |  | Alternativ 11 – Värde | Value for alternative 11 for Custom Menu 7 (CM7Alt11Value)
|  |  | Alternativ 12 – Text | Text for alternative 12 for Custom Menu 7 (CM7Alt12Text)
|  |  | Alternativ 12 – Värde | Value for alternative 12 for Custom Menu 7 (CM7Alt12Value)
|  |  | Alternativ 13 – Text | Text for alternative 13 for Custom Menu 7 (CM7Alt13Text)
|  |  | Alternativ 13 – Värde | Value for alternative 13 for Custom Menu 7 (CM7Alt13Value)
|  |  | Alternativ 14 – Text | Text for alternative 14 for Custom Menu 7 (CM7Alt14Text)
|  |  | Alternativ 14 – Värde | Value for alternative 14 for Custom Menu 7 (CM7Alt14Value)
|  |  | Alternativ 15 – Text | Text for alternative 15 for Custom Menu 7 (CM7Alt15Text)
|  |  | Alternativ 15 – Värde | Value for alternative 15 for Custom Menu 7 (CM7Alt15Value)
|  |  | Alternativ 16 – Text | Text for alternative 16 for Custom Menu 7 (CM7Alt16Text)
|  |  | Alternativ 16 – Värde | Value for alternative 16 for Custom Menu 7 (CM7Alt16Value)
|  |  | Alternativ 17 – Text | Text for alternative 17 for Custom Menu 7 (CM7Alt17Text)
|  |  | Alternativ 17 – Värde | Value for alternative 17 for Custom Menu 7 (CM7Alt17Value)
|  |  | Alternativ 18 – Text | Text for alternative 18 for Custom Menu 7 (CM7Alt18Text)
|  |  | Alternativ 18 – Värde | Value for alternative 18 for Custom Menu 7 (CM7Alt18Value)
|  |  | Alternativ 19 – Text | Text for alternative 19 for Custom Menu 7 (CM7Alt19Text)
|  |  | Alternativ 19 – Värde | Value for alternative 19 for Custom Menu 7 (CM7Alt19Value)
|  |  | Alternativ 20 – Text | Text for alternative 20 for Custom Menu 7 (CM7Alt20Text)
|  |  | Alternativ 20 – Värde | Value for alternative 20 for Custom Menu 7 (CM7Alt20Value)
|  |  | Alternativ 21 – Text | Text for alternative 21 for Custom Menu 7 (CM7Alt21Text)
|  |  | Alternativ 21 - Värde | Value for alternative 21 for Custom Menu 7 (CM7Alt21Value)
Anpassad meny 8
|  |  | Titel | Title for Custom Menu 8 (CM8Title)
|  |  | Nuvarande värde | Current value for Custom Menu 8 (CM8CurrentValue)
|  |  | Alternativ 1 – Text | Text for alternative 1 for Custom Menu 8 (CM8Alt1Text)
|  |  | Alternativ 1 – Värde | Value for alternative 1 for Custom Menu 8 (CM8Alt1Value)
|  |  | Alternativ 2 – Text | Text for alternative 2 for Custom Menu 8 (CM8Alt2Text)
|  |  | Alternativ 2 – Värde | Value for alternative 2 for Custom Menu 8 (CM8Alt2Value)
|  |  | Alternativ 3 – Text | Text for alternative 3 for Custom Menu 8 (CM8Alt3Text)
|  |  | Alternativ 3 – Värde | Value for alternative 3 for Custom Menu 8 (CM8Alt3Value)
|  |  | Alternativ 4 – Text | Text for alternative 4 for Custom Menu 8 (CM8Alt4Text)
|  |  | Alternativ 4 – Värde | Value for alternative 4 for Custom Menu 8 (CM8Alt4Value)
|  |  | Alternativ 5 – Text | Text for alternative 5 for Custom Menu 8 (CM8Alt5Text)
|  |  | Alternativ 5 – Värde | Value for alternative 5 for Custom Menu 8 (CM8Alt5Value)
|  |  | Alternativ 6 – Text | Text for alternative 6 for Custom Menu 8 (CM8Alt6Text)
|  |  | Alternativ 6 – Värde | Value for alternative 6 for Custom Menu 8 (CM8Alt6Value)
|  |  | Alternativ 7 – Text | Text for alternative 7 for Custom Menu 8 (CM8Alt7Text)
|  |  | Alternativ 7 – Värde | Value for alternative 7 for Custom Menu 8 (CM8Alt7Value)
|  |  | Alternativ 8 – Text | Text for alternative 8 for Custom Menu 8 (CM8Alt8Text)
|  |  | Alternativ 8 – Värde | Value for alternative 8 for Custom Menu 8 (CM8Alt8Value)
|  |  | Alternativ 9 – Text | Text for alternative 9 for Custom Menu 8 (CM8Alt9Text)
|  |  | Alternativ 9 – Värde | Value for alternative 9 for Custom Menu 8 (CM8Alt9Value)
|  |  | Alternativ 10 – Text | Text for alternative 10 for Custom Menu 8 (CM8Alt10Text)
|  |  | Alternativ 10 – Värde | Value for alternative 10 for Custom Menu 8 (CM8Alt10Value)
|  |  | Alternativ 11 – Text | Text for alternative 11 for Custom Menu 8 (CM8Alt11Text)
|  |  | Alternativ 11 – Värde | Value for alternative 11 for Custom Menu 8 (CM8Alt11Value)
|  |  | Alternativ 12 – Text | Text for alternative 12 for Custom Menu 8 (CM8Alt12Text)
|  |  | Alternativ 12 – Värde | Value for alternative 12 for Custom Menu 8 (CM8Alt12Value)
|  |  | Alternativ 13 – Text | Text for alternative 13 for Custom Menu 8 (CM8Alt13Text)
|  |  | Alternativ 13 – Värde | Value for alternative 13 for Custom Menu 8 (CM8Alt13Value)
|  |  | Alternativ 14 – Text | Text for alternative 14 for Custom Menu 8 (CM8Alt14Text)
|  |  | Alternativ 14 – Värde | Value for alternative 14 for Custom Menu 8 (CM8Alt14Value)
|  |  | Alternativ 15 – Text | Text for alternative 15 for Custom Menu 8 (CM8Alt15Text)
|  |  | Alternativ 15 – Värde | Value for alternative 15 for Custom Menu 8 (CM8Alt15Value)
|  |  | Alternativ 16 – Text | Text for alternative 16 for Custom Menu 8 (CM8Alt16Text)
|  |  | Alternativ 16 – Värde | Value for alternative 16 for Custom Menu 8 (CM8Alt16Value)
|  |  | Alternativ 17 – Text | Text for alternative 17 for Custom Menu 8 (CM8Alt17Text)
|  |  | Alternativ 17 – Värde | Value for alternative 17 for Custom Menu 8 (CM8Alt17Value)
|  |  | Alternativ 18 – Text | Text for alternative 18 for Custom Menu 8 (CM8Alt18Text)
|  |  | Alternativ 18 – Värde | Value for alternative 18 for Custom Menu 8 (CM8Alt18Value)
|  |  | Alternativ 19 – Text | Text for alternative 19 for Custom Menu 8 (CM8Alt19Text)
|  |  | Alternativ 19 – Värde | Value for alternative 19 for Custom Menu 8 (CM8Alt19Value)
|  |  | Alternativ 20 – Text | Text for alternative 20 for Custom Menu 8 (CM8Alt20Text)
|  |  | Alternativ 20 – Värde | Value for alternative 20 for Custom Menu 8 (CM8Alt20Value)
|  |  | Alternativ 21 – Text | Text for alternative 21 for Custom Menu 8 (CM8Alt21Text)
|  |  | Alternativ 21 - Värde | Value for alternative 21 for Custom Menu 8 (CM8Alt21Value)
Ställdon
Till/Från-utgångar
|  |  | Värmehysteres, rumstemperatur [ºC] | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Kylhysteres, rumstemperatur [ºC] | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysteres, temperatur extra zon [ºC] | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Ventilmotionering
|  |  | Ventilmotionering | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Intervall för värme [h] | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Intervall för värme 2 [h] | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Intervall för kyla [h] | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Intervall för kyla 2 [h] | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Intervall för change-over [h] | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | Intervall för 6-vägsventil [h] | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Värme, varaktighet [s] | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Värme 2, varaktighet [s] | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Kyla, varaktighet [s] | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Kyla 2, varaktighet [s] | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Change-over, varaktighet [s] | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | 6-vägsventil, varaktighet [s] | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analoga ingångar
Temperaturingång
|  |  | Filtertid [s] | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperaturingång 0–10 V
|  |  | Värde vid 0 V [°C] | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Värde vid 10 V [°C] | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2-ingång
|  |  | Värde vid 0 V [ppm] | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Värde vid 10 V [ppm] | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filtertid [s] | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Luftfuktighet ingång
|  |  | Värde vid 0 V [%] | RH at 0 Volt input (RC_RH_0V)
|  |  | Värde vid 10 V [%] | RH at 10 Volt input (RC_RH_10V)
|  |  | Filtertid [s] | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Flödesingång
|  |  | Värde vid 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Värde vid 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filtertid [s] | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC-ingång
|  |  | Värde vid 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Värde vid 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filtertid [s] | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Börvärden
Rumsbörvärden
|  |  | Värme, occupied [°C] | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Kyla, occupied [°C] | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Värme, standby [°C] | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Kyla, standby [°C] | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Värme, unoccupied [°C] | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Kyla, unoccupied [°C] | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Frostskydd [°C] | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Börvärdesjustering
|  |  | Max. justering uppåt [°C] | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Max. justering nedåt [°C] | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Börvärdesjustering [°C] | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Extra zon
|  |  | Extra zon, börvärde [°C] | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2-börvärde [ppm] | Setpoint for CO2 control (RC_CO2Setpoint)
Luftfuktighet
|  |  | Fuktighetsbörvärde [%] | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC-börvärde | Setpoint for VOC control (RC_VOCSetpoint)
Regulatorinställningar
Rum
|  |  | P-band [°C] | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-tid [s] | I-time for room PID controller (RC_RoomPIDItime)
Kaskadreglering
|  |  | Reglering aktiv | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Kaskadfaktor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Max. temperatur värme [°C] | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min. temperatur värme [°C] | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Max. temperatur kyla [°C] | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min. temperatur kyla [°C] | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Frostskyddstemperatur [°C] | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Extra zon
|  |  | P-band [°C] | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-tid [s] | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-band [ppm] | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-tid [s] | I-time for CO2 PID controller (RC_CO2PIDItime)
Luftfuktighet
|  |  | P-band [%] | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-tid [s] | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-band | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-tid [s] | I-time for VOC PID controller (RC_VOCPIDItime)
Larminställningar
Larm rumstemperatur
|  |  | Högt gränsvärde [°C] | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Lågt gränsvärde [°C] | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
Larm CO2-nivå
|  |  | Högt gränsvärde [ppm] | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Ingångsjusteringar
UI1
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Offsetjustering | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Offsetjustering | Offset for input (IoAnaIn_2_offset)
Rumstemperatur
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Offsetjustering | Offset for input (IoAnaIn_5_offset)
Luftfuktighet i rum
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Offsetjustering | Offset for input (IoAnaIn_6_offset)
VOC-givare
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Offsetjustering | Offset for input (IoAnaIn_7_offset)
CO2-givare
|  |  | Gränsvärdeshantering | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Offsetjustering | Offset for input (IoAnaIn_8_offset)
Utgångsjusteringar
UO1
|  |  | Minimivärde | Scale for output (IoAnaOut_1_min_in)
|  |  | Maxvärde | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimivärde [0=0%, 100=100%] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maxvärde [0=0%, 100=100%] | Scale for output (IoAnaOut_1_max_out)
|  |  | Förskjutning baserad på fullt intervall [-100=-100%, 100=100%] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Minimivärde | Scale for output (IoAnaOut_2_min_in)
|  |  | Maxvärde | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimivärde [0=0%, 100=100%] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maxvärde [0=0%, 100=100%] | Scale for output (IoAnaOut_2_max_out)
|  |  | Förskjutning baserad på fullt intervall [-100=-100%, 100=100%] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Minimivärde | Scale for output (IoAnaOut_3_min_in)
|  |  | Maxvärde | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimivärde [0=0%, 100=100%] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maxvärde [0=0%, 100=100%] | Scale for output (IoAnaOut_3_max_out)
|  |  | Förskjutning baserad på fullt intervall [-100=-100%, 100=100%] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Minimivärde | Scale for output (IoAnaOut_4_min_in)
|  |  | Maxvärde | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimivärde [0=0%, 100=100%] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maxvärde [0=0%, 100=100%] | Scale for output (IoAnaOut_4_max_out)
|  |  | Förskjutning baserad på fullt intervall [-100=-100%, 100=100%] | Offset for output (IoAnaOut_4_offset)
Manuell/Auto
Fjärringångsvärden
Rumstemperatur
|  |  | Fjärrinställning | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Inställt värde [°C] | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Rumstemperatur [°C] | Room temperature (RC_RoomTemp)
Tilluftstemperatur
|  |  | Fjärrinställning | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Inställt värde [°C] | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Tilluftstemperatur [°C] | Supply air temperature (RC_SupplyAirTemp)
Extra zon, temperatur
|  |  | Fjärrinställning | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Inställt värde [°C] | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Extra zon, temperatur [°C] | Extra Zone temperature (RC_ExtraZoneTemp)
Change-over-temperatur
|  |  | Fjärrinställning | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Inställt värde [°C] | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-over-temperatur [°C] | Changeover temperature (RC_ChangeOverTemp)
Change-over VAV-temperatur
|  |  | Fjärrinställning | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Inställt värde [°C] | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-over VAV-temperatur [°C] | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2-nivå
|  |  | Fjärrinställning | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Inställt värde [ppm] | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2-nivå [ppm] | Room CO2 level (RC_CO2Level)
Luftfuktighet i rum
|  |  | Fjärrinställning | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Inställt värde [%] | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Luftfuktighet i rum [%] | Relative humidity (RC_Humidity)
Luftflöde
|  |  | Fjärrinställning | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Inställt värde | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Luftflöde | Air flow (RC_AirFlow)
VOC-index
|  |  | Fjärrinställning | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Inställt värde | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC-index | VOC index (RC_VOC)
Närvarostyrning
|  |  | Fjärrinställning | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Inställt värde | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Närvarostyrning | Presence indication (RC_Presence)
Öppet fönster
|  |  | Fjärrinställning | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Inställt värde | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Öppet fönster | Open window indication (RC_DIOpenWindow)
Kondensation
|  |  | Fjärrinställning | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Inställt värde | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Kondensation | Condensation indication (RC_DICondensation)
Externt larm (DI)
|  |  | Fjärrinställning | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Inställt värde | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | Externt larm (DI) | Digital input alarm (RC_AlarmDI)
Change-over DI
|  |  | Fjärrinställning | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Inställt värde | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-over DI | Change-over digital input (RC_DIChangeOver)
Change-over VAV DI
|  |  | Fjärrinställning | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Inställt värde | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-over VAV DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Manuell/Auto
Regulatorläge
|  |  | Regulatorläge | Current state (RC_ControllerState)
|  |  | Fjärrlägesinställning | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Shutdown | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Forcerad ventilation | Set controller in Bypass state (RC_ControllerStateSetBypass)
Fläktregleringskälla
|  |  | Fläktregleringskälla | Fan speed setting (RC_FanSelect)
Värme-utgång
|  |  | Driftläge | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Inställt värde [%] | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Värme-utgång [%] | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Driftläge | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Värme-utgång | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Värme 2-utgång
|  |  | Driftläge | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Inställt värde [%] | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Värme 2-utgång [%] | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Driftläge | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Värme 2-utgång | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Kyla-utgång
|  |  | Driftläge | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Inställt värde [%] | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Kyla-utgång [%] | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Driftläge | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Kyla-utgång | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Kyla 2-utgång
|  |  | Driftläge | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Inställt värde [%] | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Kyla 2-utgång [%] | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Driftläge | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Kyla 2-utgång | Room control Cool2 output digital (RC_RoomCool2OutputDO)
VAV-utgång
|  |  | Driftläge | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Inställt värde [%] | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | VAV-utgång [%] | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
VAV 2-utgång
|  |  | Driftläge | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Inställt värde [%] | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | VAV 2-utgång [%] | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Change-over-utgång
|  |  | Driftläge | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Inställt värde [%] | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Change-over-utgång [%] | Room control Change over output analog (RC_RoomChangeOverOutputAO)
VAV-utgång för change-over
|  |  | Driftläge | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Inställt värde [%] | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | VAV-utgång för change-over [%] | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
Utgång för 6-vägsventil
|  |  | Driftläge | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Driftläge | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Inställt värde [%] | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | Utgång för 6-vägsventil [%] | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Utgång för extra zon
|  |  | Driftläge | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Inställt värde [%] | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Utgång för extra zon | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC-fläktreglering
|  |  | Driftläge | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Inställt värde [%] | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC-fläktreglering [%] | Current EC fan speed (RC_ECFanSpeed)
Utgång för CO2-reglering
|  |  | Driftläge | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Inställt värde [%] | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | Utgång för CO2-reglering [%] | CO2 control analog out (RC_CO2ControlAO)
Utgång för fuktreglering
|  |  | Driftläge | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Inställt värde [%] | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Utgång för fuktreglering [%] | Humidify analog out (RC_HumidifyOutputAO)
Utgång för avfuktningsreglering
|  |  | Driftläge | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Inställt värde [%] | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Utgång för avfuktningsreglering [%] | Dehumidify analog out (RC_DehumidifyOutputAO)
Utgång för VOC-reglering
|  |  | Driftläge | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Inställt värde [%] | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | Utgång för VOC-reglering [%] | VOC control analog out (RC_VOCControlAO)
Aktiv utgång för extra zon
|  |  | Driftläge | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Aktiv utgång för extra zon | Extra Zone active (RC_ExtraZoneActive)
Utgång för forcerad ventilation
|  |  | Driftläge | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Utgång för forcerad ventilation | Forced ventilation output (RC_ForcedVentDO)
Hårdvarustyrning
UO1
|  |  | UO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Driftläge | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Inställt värde [0=0%, 100=100%] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Driftläge | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Inställt värde | Override value (IoDo_1_override)
UO2
|  |  | UO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Driftläge | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Inställt värde [0=0%, 100=100%] | Override value (IoAnaOut_2_override)
|  |  | UO2: | Value set for output (IoDo_2_value)
|  |  | Driftläge | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Inställt värde | Override value (IoDo_2_override)
AO1
|  |  | AO1: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Driftläge | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Inställt värde [0=0%, 100=100%] | Override value (IoAnaOut_3_override)
AO2
|  |  | AO2: [V] | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Driftläge | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Inställt värde [0=0%, 100=100%] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Driftläge | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Inställt värde | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Driftläge | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Inställt värde | Override value (IoAnaIn_2_override)
Kalibrering av CO2-givare
|  |  | Aktivera automatisk självkalibrering | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | Baseline för automatisk självkalibrering [ppm] [ppm] | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | Kör forcerad Omkalibrering av CO2-givare | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | Referensnivå för CO2 vid forcerad omkalibrering [ppm] [ppm] | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | Senaste forcerade omkalibreringsförskjutning (-9999 = Fel) | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | Återställ CO2-givare | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Reläutgång
|  |  | Relästatus | Value set for output (IoDo_3_value)
|  |  | Driftläge | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Inställt värde | Override value (IoDo_3_override)
PIR-givare
|  |  | PIR-givare | Filtered value from sensor (IoDiIn_4_value)
|  |  | Driftläge | Set to 1 to enable override (IoDiIn_4_override_en)
|  |  | Inställt värde | Override value (IoDiIn_4_override)
Enhet
Enhets-ID
Enhets-ID
|  |  | Namn | (ControllerName)
|  |  | Beskrivning | Controller description (ControllerDescription)
|  |  | Plats | Controller location (ControllerLocation)
|  |  | Projekt | (ControllerProject)
Kommunikation
Portinställningar
|  |  | Port 1 funktion | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Baudhastighet, port 1 | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Paritet, port 1 | Comm. format Port 1 (RS485) (RC_Port1Format)
EXOline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbusadress | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | MSTP-adress för BACnet | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | Högsta master-adress för MSTP | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet enhets-ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet-enhetens objektnamn | BACnet device object name (BACnetDeviceObjectName)
|  |  | Lösenord | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth-funktion | Function for BLE button (BleButtonMode)
|  |  | Stäng av efter [s] | Timeout when BLE is started with the button (BleButtonTimeout)
|  |  | BLE-sändningseffekt | BLE TX power level (ble_power)
Kommunikationsfel
|  |  | Felhantering | Offline function (RC_OfflineFunction)
|  |  | Avbrott [s] | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Reservläge | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Återställ
Återställ
|  |  | Starta om regulator | Write to this register will trigger resets with different reset reasons (product_reset)
Icke-flyktig lagring
Icke-flyktig lagring
|  |  | Inaktivera icke-flyktig lagring | Set to 1 to disable storage in non volatile memory (disable_nv_storage)