## Variables
RCX-… 2.0-1-xx ꟷ Variable list | [15 empty] | Revision: | A
|  |  | EXOline |  |  | Modbus | [6 empty] | BACnet
Name | Default | Description | Type | Load | Cell | Reg. Type | RW | Register | Addr | Data Type | Scale | Offset | Object type | Instance | Unit | Writeable | Variable type
ModbusListVersion |  | Modbus list version | X | 1 | 0 | Input | R | 300001 | 0 | U8
product_reset | 0 | Write to this register will trigger resets with different reset reasons | I | 1 | 1
rc_wink | 0 | Wink for this amount of time in seconds | X | 1 | 3 | Holding | RW | 400003 | 2 | U8 |  |  | positive_integer_value | 9011 |  | X
RC_CommSettingsCommit | 0 | Commit communication settings | L | 1 | 5 | Coil | RW | 000001 | 0 | LOGIC |  |  | binary_value | 9001 |  | X
RC_Port1Mode | 2 | Comm. protocol Port 1 (RS485) | X | 1 | 6 | Holding | RW | 400005 | 4 | U8 |  |  | multi_state_value | 9001 |  | X
RC_Port1Baud | 0 | Comm. speed Port 1 (RS485) | X | 1 | 7 | Holding | RW | 400007 | 6 | U8 |  |  | multi_state_value | 9101 |  | X
RC_Port1Format | 112 | Comm. format Port 1 (RS485) | X | 1 | 8 | Holding | RW | 400006 | 5 | U8 |  |  | multi_state_value | 9201 |  | X
SerialHigh |  | Serial number, high part | I | 1 | 15 | Input | R | 300005 | 4 | I16
SerialMid |  | Serial number, mid part | I | 1 | 17 | Input | R | 300004 | 3 | I16
SerialLow |  | Serial number, low part | I | 1 | 19 | Input | R | 300003 | 2 | I16
RC_Offline |  | Heartbeat function indicates if the device is offline or not | L | 1 | 21 | Discrete | R | 100001 | 0 | LOGIC
RC_OfflineTrigger | 0 | Write 1 to this register periodically for keep system running in normal mode, will be set to 0 by application | L | 1 | 22 | Coil | RW | 000002 | 1 | LOGIC |  |  | binary_value | 9101 |  | X
RC_OfflineFunction | 0 | Offline function | X | 1 | 23 | Holding | RW | 400020 | 19 | U8 |  |  | multi_state_value | 9301 |  | X
RC_OfflineCounter |  | Offline timeout counter seconds. Used to check current state of the counter, it counts from 0 at trigger up to next trigger or HEARTBEAT_OFFLINE_TIMEOUT. | I | 1 | 24 | Input | R | 300010 | 9 | I16
RC_OfflineTimeout | 10 | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. | I | 1 | 26 | Holding | RW | 400021 | 20 | I16
RgbEnable | 0 | Set to True to enable the external control of the LED | L | 1 | 35 | Coil | RW | 000003 | 2 | LOGIC
RgbOffColor | 0 | 8 bit color for when the LED is in state Off (0bRRRGGGBB) | X | 1 | 36 | Holding | RW | 400027 | 26 | U8
RgbOffTime | 500 | Off time in ms | I | 1 | 37 | Holding | RW | 400028 | 27 | I16
RgbOnColor | 252 | 8 bit color for when the LED is in state On (0bRRRGGGBB) | X | 1 | 39 | Holding | RW | 400029 | 28 | U8
RgbOnTime | 100 | On time in ms | I | 1 | 40 | Holding | RW | 400030 | 29 | I16
product_status | 0 | Bit field, See Description on Global device Status | I | 1 | 58 | Holding | RW | 400004 | 3 | I16
OspreyVerMajor |  | Osprey version, major part | X | 1 | 64 | Input | R | 300013 | 12 | U8
OspreyVerMinor |  | Osprey version, minor part | X | 1 | 65 | Input | R | 300014 | 13 | U8
OspreyVerBranch |  | Osprey version, branch part | X | 1 | 66 | Input | R | 300015 | 14 | U8
OspreyVerNumber |  | Osprey version, number part | X | 1 | 67 | Input | R | 300016 | 15 | U8
OspreyGitCommit |  | Osprey Git commit | I | 1 | 68 | Input | R | 300017 | 16 | I16
OsId |  | Application OPERATING_SYSTEM_ID | I | 1 | 70 | Input | R | 300021 | 20 | I16
VersionNumberString |  | The application version as a string | $ | 1 | 76
gitCommitHashString |  | The Full Git hash of the application | $ | 1 | 79
BleButtonMode | 3 | Function for BLE button | X | 1 | 83 | Holding | RW | 400071 | 70 | U8
BleButtonTimeout | 120 | Timeout when BLE is started with the button | I | 1 | 84 | Holding | RW | 400072 | 71 | I16
BleVerMajor |  | BLE stack version, major part | X | 1 | 98 | Input | R | 300022 | 21 | U8
BleVerMinor |  | BLE stack version, minor part | X | 1 | 99 | Input | R | 300023 | 22 | U8
BleVerBranch |  | BLE stack version, branch part | X | 1 | 100 | Input | R | 300024 | 23 | U8
BleVerNumber |  | BLE stack version, number part | X | 1 | 101 | Input | R | 300025 | 24 | U8
FusVerMajor |  | FUS stack version, major part | X | 1 | 102 | Input | R | 300026 | 25 | U8
FusVerMinor |  | FUS version, minor part | X | 1 | 103 | Input | R | 300027 | 26 | U8
FusVerBranch |  | FUS version, branch part | X | 1 | 104 | Input | R | 300028 | 27 | U8
FusVerNumber |  | FUS version, number part | X | 1 | 105 | Input | R | 300029 | 28 | U8
RC_RoomTemp |  | Room temperature | R | 2 | 0 | Input | R | 305001 | 5000 | I16SO | 10 | 0 | analog_value | 10001 | degrees_celsius
RC_CO2Level |  | Room CO2 level | R | 2 | 3 | Input | R | 305002 | 5001 | I16SO | 1 | 0 | analog_value | 10011 | parts_per_million
RC_AirFlow |  | Air flow | R | 2 | 6 | Input | R | 305003 | 5002 | I16SO | 1 | 0 | analog_value | 10021 | REG_FLOW_UNIT
RC_ChangeOverTemp |  | Changeover temperature | R | 2 | 9 | Input | R | 305004 | 5003 | I16SO | 10 | 0 | analog_value | 10031 | degrees_celsius
RC_ChangeOverVAVTemp |  | Changeover VAV temperature | R | 2 | 12 | Input | R | 305005 | 5004 | I16SO | 10 | 0 | analog_value | 10041 | degrees_celsius
RC_ExtraZoneTemp |  | Extra Zone temperature | R | 2 | 15 | Input | R | 305006 | 5005 | I16SO | 10 | 0 | analog_value | 10051 | degrees_celsius
RC_SupplyAirTemp |  | Supply air temperature | R | 2 | 18 | Input | R | 305007 | 5006 | I16SO | 10 | 0 | analog_value | 10061 | degrees_celsius
RC_Humidity |  | Relative humidity | R | 2 | 21 | Input | R | 305008 | 5007 | I16SO | 10 | 0 | analog_value | 10071 | percent_relative_humidity
RC_Presence |  | Presence indication | L | 2 | 24 | Discrete | R | 105001 | 5000 | LOGIC |  |  | binary_value | 10001
RC_DIPresence |  | DI Presence indication | L | 2 | 25 | Discrete | R | 105002 | 5001 | LOGIC |  |  | binary_value | 10011
RC_CO2Presence |  | CO2 Presence indication | L | 2 | 26 | Discrete | R | 105003 | 5002 | LOGIC |  |  | binary_value | 10021
RC_DIOpenWindow |  | Open window indication | L | 2 | 27 | Discrete | R | 105004 | 5003 | LOGIC |  |  | binary_value | 10031
RC_DIChangeOver |  | Change-over digital input | L | 2 | 28 | Discrete | R | 105005 | 5004 | LOGIC |  |  | binary_value | 10041
RC_DIChangeOverVAV |  | Change-over VAV digital input | L | 2 | 29 | Discrete | R | 105006 | 5005 | LOGIC |  |  | binary_value | 10051
RC_DICondensation |  | Condensation indication | L | 2 | 30 | Discrete | R | 105007 | 5006 | LOGIC |  |  | binary_value | 10061
RC_RoomActiveSetpoint |  | Active room control setpoint | R | 2 | 31 | Input | R | 305009 | 5008 | I16SO | 10 | 0 | analog_value | 10081 | degrees_celsius
RC_SupplyAirSetpoint |  | Active supply air setpoint | R | 2 | 34 | Input | R | 305010 | 5009 | I16SO | 10 | 0 | analog_value | 10091 | degrees_celsius
RC_ControllerState |  | Current state | X | 2 | 37 | Input | R | 305011 | 5010 | U8 |  |  | multi_state_value | 10001
RC_ControllerMode |  | Current controller mode | X | 2 | 38 | Input | R | 305012 | 5011 | U8 |  |  | multi_state_value | 10011
RC_ChangeOverState |  | Change-over status | L | 2 | 39 | Discrete | R | 105008 | 5007 | LOGIC |  |  | binary_value | 10071
RC_ChangeOverStateVAV |  | Change-over VAV status | L | 2 | 40 | Discrete | R | 105009 | 5008 | LOGIC |  |  | binary_value | 10081
RC_ExtraZoneActive |  | Extra Zone active | L | 2 | 41 | Discrete | R | 105010 | 5009 | LOGIC |  |  | binary_value | 10091
RC_RoomHeat1OutputAO |  | Room control Heat1 output analog | X | 2 | 42 | Input | R | 305013 | 5012 | U8 |  |  | analog_value | 10101 | percent
RC_RoomCool1OutputAO |  | Room control Cool1 output analog | X | 2 | 43 | Input | R | 305014 | 5013 | U8 |  |  | analog_value | 10111 | percent
RC_RoomVAV1OutputAO |  | Room control VAV1 output analog | X | 2 | 44 | Input | R | 305015 | 5014 | U8 |  |  | analog_value | 10121 | percent
RC_RoomHeat2OutputAO |  | Room control Heat2 output analog | X | 2 | 45 | Input | R | 305016 | 5015 | U8 |  |  | analog_value | 10131 | percent
RC_RoomCool2OutputAO |  | Room control Cool2 output analog | X | 2 | 46 | Input | R | 305017 | 5016 | U8 |  |  | analog_value | 10141 | percent
RC_RoomVAV2OutputAO |  | Room control VAV2 output analog | X | 2 | 47 | Input | R | 305018 | 5017 | U8 |  |  | analog_value | 10151 | percent
RC_RoomChangeOverOutputAO |  | Room control Change over output analog | X | 2 | 48 | Input | R | 305019 | 5018 | U8 |  |  | analog_value | 10161 | percent
RC_Room6WayValveOutputAO |  | Room control 6-way valve output analog | X | 2 | 49 | Input | R | 305020 | 5019 | U8 |  |  | analog_value | 10171 | percent
RC_RoomChangeOverVAVOutputAO |  | Room control Change over VAV output analog | X | 2 | 50 | Input | R | 305021 | 5020 | U8 |  |  | analog_value | 10181 | percent
RC_ExtraZoneOutputAO |  | Extra Zone output analog | X | 2 | 51 | Input | R | 305022 | 5021 | U8 |  |  | analog_value | 10191 | percent
RC_ECFanSpeed |  | Current EC fan speed | X | 2 | 52 | Input | R | 305023 | 5022 | U8 |  |  | analog_value | 10201 | percent
RC_CO2ControlAO |  | CO2 control analog out | X | 2 | 53 | Input | R | 305024 | 5023 | U8 |  |  | analog_value | 10211 | percent
RC_HumidifyOutputAO |  | Humidify analog out | X | 2 | 54 | Input | R | 305025 | 5024 | U8 |  |  | analog_value | 10221 | percent
RC_DehumidifyOutputAO |  | Dehumidify analog out | X | 2 | 55 | Input | R | 305026 | 5025 | U8 |  |  | analog_value | 10231 | percent
RC_AirflowControlAO |  | Airflow control analog out | X | 2 | 56 | Input | R | 305027 | 5026 | U8
RC_PIDHeatDemand |  | Room PID heat output | X | 2 | 57 | Input | R | 305028 | 5027 | U8 |  |  | analog_value | 10241 | percent
RC_PIDCoolDemand |  | Room PID cool output | X | 2 | 58 | Input | R | 305029 | 5028 | U8 |  |  | analog_value | 10251 | percent
RC_RoomHeat1OutputDO |  | Room control Heat1 output digital | L | 2 | 59 | Discrete | R | 105011 | 5010 | LOGIC |  |  | binary_value | 10101
RC_RoomCool1OutputDO |  | Room control Cool1 output digital | L | 2 | 60 | Discrete | R | 105012 | 5011 | LOGIC |  |  | binary_value | 10111
RC_RoomVAV1OutputDO |  | Room control VAV1 output digital | L | 2 | 61 | Discrete | R | 105013 | 5012 | LOGIC |  |  | binary_value | 10121
RC_RoomHeat2OutputDO |  | Room control Heat2 output digital | L | 2 | 62 | Discrete | R | 105014 | 5013 | LOGIC |  |  | binary_value | 10131
RC_RoomCool2OutputDO |  | Room control Cool2 output digital | L | 2 | 63 | Discrete | R | 105015 | 5014 | LOGIC |  |  | binary_value | 10141
RC_RoomVAV2OutputDO |  | Room control VAV2 output digital | L | 2 | 64 | Discrete | R | 105016 | 5015 | LOGIC |  |  | binary_value | 10151
RC_RoomChangeOverOutputDO |  | Room control Change over output digital | L | 2 | 65 | Discrete | R | 105017 | 5016 | LOGIC |  |  | binary_value | 10161
RC_Room6WayValveOutputDO |  | Room control 6-way valve output digital | L | 2 | 66 | Discrete | R | 105018 | 5017 | LOGIC |  |  | binary_value | 10171
RC_RoomChangeOverVAVOutputDO |  | Room control Change over VAV output digital | L | 2 | 67 | Discrete | R | 105019 | 5018 | LOGIC |  |  | binary_value | 10181
RC_ExtraZoneOutputDO |  | Extra Zone output digital | L | 2 | 68 | Discrete | R | 105020 | 5019 | LOGIC |  |  | binary_value | 10191
RC_CO2ControlDO |  | CO2 control digital out | L | 2 | 69 | Discrete | R | 105021 | 5020 | LOGIC |  |  | binary_value | 10201
RC_HumidifyOutputDO |  | Humidify digital out | L | 2 | 70 | Discrete | R | 105022 | 5021 | LOGIC |  |  | binary_value | 10211
RC_DehumidifyOutputDO |  | Dehumidify digital out | L | 2 | 71 | Discrete | R | 105023 | 5022 | LOGIC |  |  | binary_value | 10221
RC_AirflowControlDO |  | Airflow control digital out | L | 2 | 72 | Discrete | R | 105024 | 5023 | LOGIC
RC_FanSpeed |  | Current 3-speed fan speed | X | 2 | 73 | Input | R | 305030 | 5029 | U8
RC_FanSpeed1DO |  | Fan speed 1 output | L | 2 | 74 | Discrete | R | 105025 | 5024 | LOGIC
RC_FanSpeed2DO |  | Fan speed 2 output | L | 2 | 75 | Discrete | R | 105026 | 5025 | LOGIC
RC_FanSpeed3DO |  | Fan speed 3 output | L | 2 | 76 | Discrete | R | 105027 | 5026 | LOGIC
RC_ForcedVentDO |  | Forced ventilation output | L | 2 | 77 | Discrete | R | 105028 | 5027 | LOGIC |  |  | binary_value | 10231
RC_AlarmRoomTempHigh |  | High room temp alarm | L | 2 | 78 | Discrete | R | 105029 | 5028 | LOGIC |  |  | binary_value | 10241
RC_AlarmRoomTempLow |  | Low room temp alarm | L | 2 | 79 | Discrete | R | 105030 | 5029 | LOGIC |  |  | binary_value | 10251
RC_AlarmCO2High |  | High CO2 alarm | L | 2 | 80 | Discrete | R | 105031 | 5030 | LOGIC |  |  | binary_value | 10261
RC_DamperPosition |  | Damper position | R | 2 | 81 | Input | R | 305031 | 5030 | I16SO | 10 | 0 | analog_value | 10261
RC_ExtractTemperature |  | Extract temperature | R | 2 | 84 | Input | R | 305032 | 5031 | I16SO | 10 | 0 | analog_value | 10271 | degrees_celsius
RC_VOC |  | VOC index | R | 2 | 87 | Input | R | 305033 | 5032 | I16SO | 10 | 0 | analog_value | 10281
RC_DisplayViewValue |  | Value to be shown in the display | R | 2 | 90 | Input | R | 305034 | 5033 | I16SO | 10 | 0 | analog_value | 10291
RC_DisplaySetpointValue |  | Setpoint display at setpoint adjustment | R | 2 | 93 | Input | R | 305035 | 5034 | I16SO | 10 | 0 | analog_value | 10301
RC_CO2Indicator |  | RGB CO2 indication | X | 2 | 96 | Input | R | 305036 | 5035 | U8 |  |  | multi_state_value | 10021
RC_LightingDO |  | Light control output | L | 2 | 97 | Discrete | R | 105032 | 5031 | LOGIC
RC_SumAlarm |  | Sum Alarm | L | 2 | 98 | Discrete | R | 105033 | 5032 | LOGIC |  |  | binary_value | 10271
RC_CO2LevelRounded |  | Rounded room CO2 level | R | 2 | 99 | Input | R | 305037 | 5036 | I16SO | 1 | 0 | analog_value | 10311 | parts_per_million
RC_VOCControlAO |  | VOC control analog out | X | 2 | 102 | Input | R | 305038 | 5037 | U8 |  |  | analog_value | 10321 | percent
RC_VOCControlDO |  | VOC control digital out | L | 2 | 103 | Discrete | R | 105034 | 5033 | LOGIC |  |  | binary_value | 10281
RC_AlarmSensorError |  | Sensor error alarm | L | 2 | 104 | Discrete | R | 105035 | 5034 | LOGIC |  |  | binary_value | 10291
RC_AlarmDI |  | Digital input alarm | L | 2 | 105 | Discrete | R | 105036 | 5035 | LOGIC |  |  | binary_value | 10301
RC_AlarmManualOutput |  | Alarm when an output is set to manual | L | 2 | 106 | Discrete | R | 105037 | 5036 | LOGIC |  |  | binary_value | 10311
RC_UI1Func | 0 | UI1 Input function | X | 3 | 0 | Holding | RW | 405001 | 5000 | U8
RC_UI2Func | 0 | UI2 Input function | X | 3 | 1 | Holding | RW | 405002 | 5001 | U8
RC_UI3Func | 0 | UI3 Input function | X | 3 | 2 | Holding | RW | 405003 | 5002 | U8
RC_UI4Func | 0 | UI4 Input function | X | 3 | 3 | Holding | RW | 405004 | 5003 | U8
RC_UO1Func | 0 | UO1 Output function | X | 3 | 20 | Holding | RW | 405021 | 5020 | U8
RC_UO2Func | 0 | UO2 Output function | X | 3 | 21 | Holding | RW | 405022 | 5021 | U8
RC_UO3Func | 0 | UO3 Output function | X | 3 | 22 | Holding | RW | 405023 | 5022 | U8
RC_UO4Func | 0 | UO4 Output function | X | 3 | 23 | Holding | RW | 405024 | 5023 | U8
RC_RoomSeq1Function | 0 | Room sequence step 1 function | X | 3 | 100 | Holding | RW | 405101 | 5100 | U8
RC_RoomSeq2Function | 0 | Room sequence step 2 function | X | 3 | 101 | Holding | RW | 405102 | 5101 | U8
RC_RoomSeq3Function | 0 | Room sequence step 3 function | X | 3 | 102 | Holding | RW | 405103 | 5102 | U8
RC_Heat1OutputMax | 100 | Heat1 maximum output for all controller states. | X | 3 | 103 | Holding | RW | 405104 | 5103 | U8
RC_Heat2OutputMax | 100 | Heat2 maximum output for all controller states. | X | 3 | 104 | Holding | RW | 405105 | 5104 | U8
RC_Heat1OutputMin | 0 | Heat1 minimum output for all controller states. | X | 3 | 105 | Holding | RW | 405106 | 5105 | U8
RC_Heat2OutputMin | 0 | Heat2 minimum output for all controller states. | X | 3 | 106 | Holding | RW | 405107 | 5106 | U8
RC_Heat1Afterblow | 0 | Heat1 enable afterblow function | L | 3 | 107 | Coil | RW | 005001 | 5000 | LOGIC
RC_Heat2Afterblow | 0 | Heat2 enable afterblow function | L | 3 | 108 | Coil | RW | 005002 | 5001 | LOGIC
RC_Cool1OutputMax | 100 | Cool1 maximum output for all controller states. | X | 3 | 109 | Holding | RW | 405108 | 5107 | U8
RC_Cool2OutputMax | 100 | Cool2 maximum output for all controller states. | X | 3 | 110 | Holding | RW | 405109 | 5108 | U8
RC_Cool1OutputMin | 0 | Cool1 minimum output for all controller states. | X | 3 | 111 | Holding | RW | 405110 | 5109 | U8
RC_Cool2OutputMin | 0 | Cool2 minimum output for all controller states. | X | 3 | 112 | Holding | RW | 405111 | 5110 | U8
RC_Cool1OutputMaxWhenForced | 0 | Set Cool1 output to max value when forced ventilation is active | L | 3 | 113 | Coil | RW | 005003 | 5002 | LOGIC
RC_Cool2OutputMaxWhenForced | 0 | Set Cool2 output to max value when forced ventilation is active | L | 3 | 114 | Coil | RW | 005004 | 5003 | LOGIC
RC_VAV1OutputMax | 100 | VAV1 maximum output for all controller states. | X | 3 | 115 | Holding | RW | 405112 | 5111 | U8
RC_VAV2OutputMax | 100 | VAV2 maximum output for all controller states. | X | 3 | 116 | Holding | RW | 405113 | 5112 | U8
RC_VAV1OutputMinOff | 0 | VAV1 minimum output in Off state. | X | 3 | 117 | Holding | RW | 405114 | 5113 | U8
RC_VAV2OutputMinOff | 0 | VAV2 minimum output in Off state. | X | 3 | 118 | Holding | RW | 405115 | 5114 | U8
RC_VAV1OutputMinUnoccupied | 10 | VAV1 minimum output in Unoccupied state. | X | 3 | 119 | Holding | RW | 405116 | 5115 | U8
RC_VAV2OutputMinUnoccupied | 10 | VAV2 minimum output in Unoccupied state. | X | 3 | 120 | Holding | RW | 405117 | 5116 | U8
RC_VAV1OutputMinStandby | 10 | VAV1 minimum output in Standby state. | X | 3 | 121 | Holding | RW | 405118 | 5117 | U8
RC_VAV2OutputMinStandby | 10 | VAV2 minimum output in Standby state. | X | 3 | 122 | Holding | RW | 405119 | 5118 | U8
RC_VAV1OutputMinOccupied | 20 | VAV1 minimum output in Occupied state | X | 3 | 123 | Holding | RW | 405120 | 5119 | U8
RC_VAV2OutputMinOccupied | 20 | VAV2 minimum output in Occupied state | X | 3 | 124 | Holding | RW | 405121 | 5120 | U8
RC_VAV1OutputMinBypass | 20 | VAV1 minimum output in Bypass state. | X | 3 | 125 | Holding | RW | 405122 | 5121 | U8
RC_VAV2OutputMinBypass | 20 | VAV2 minimum output in Bypass state. | X | 3 | 126 | Holding | RW | 405123 | 5122 | U8
RC_VAV1OutputMaxWhenForced | 0 | Set VAV1 output to max value when forced ventilation is active | L | 3 | 127 | Coil | RW | 005005 | 5004 | LOGIC
RC_VAV2OutputMaxWhenForced | 0 | Set VAV2 output to max value when forced ventilation is active | L | 3 | 128 | Coil | RW | 005006 | 5005 | LOGIC
RC_VAV1OutputMaxHeat | 0 | VAV1 maximum output when the controller is in heating mode. | X | 3 | 129 | Holding | RW | 405124 | 5123 | U8
RC_ChangeOverVAVOutputMax | 100 | ChangeOverVAV maximum output for all controller states. | X | 3 | 130 | Holding | RW | 405125 | 5124 | U8
RC_ChangeOverVAVOutputMinOff | 0 | ChangeOverVAV minimum output in Off state. | X | 3 | 131 | Holding | RW | 405126 | 5125 | U8
RC_ChangeOverVAVOutputMinUnoccupied | 10 | ChangeOverVAV minimum output in Unoccupied state. | X | 3 | 132 | Holding | RW | 405127 | 5126 | U8
RC_ChangeOverVAVOutputMinStandby | 10 | ChangeOverVAV minimum output in Standby state. | X | 3 | 133 | Holding | RW | 405128 | 5127 | U8
RC_ChangeOverVAVOutputMinOccupied | 20 | ChangeOverVAV minimum output in Occupied state | X | 3 | 134 | Holding | RW | 405129 | 5128 | U8
RC_ChangeOverVAVOutputMinBypass | 20 | ChangeOverVAV minimum output in Bypass state. | X | 3 | 135 | Holding | RW | 405130 | 5129 | U8
RC_ChangeOverVAVOutputMaxWhenForced | 0 | Set ChangeOverVAV output to max value when forced ventilation is active | L | 3 | 136 | Coil | RW | 005007 | 5006 | LOGIC
RC_VAVControlCooling | 1 | VAV is controlled by cooling output | L | 3 | 137 | Coil | RW | 005008 | 5007 | LOGIC
RC_VAVControlCO2 | 0 | VAV is controlled by CO2 output | L | 3 | 138 | Coil | RW | 005009 | 5008 | LOGIC
RC_ChangeOverOutputMax | 100 | Changeover maximum output for all controller states. | X | 3 | 141 | Holding | RW | 405131 | 5130 | U8
RC_ChangeOverOutputMin | 0 | Changeover minimum output for all controller states. | X | 3 | 142 | Holding | RW | 405132 | 5131 | U8
RC_ChangeOverSelect | 0 | Type of detection to control change-over. | X | 3 | 143 | Holding | RW | 405133 | 5132 | U8 |  |  | multi_state_value | 10422 |  | X
RC_ChangeOverTemperature | 22 | The reference temperature to use in simple mode, in advanced mode the room temperature is used | R | 3 | 144 | Holding | RW | 405134 | 5133 | I16SO | 10 | 0
RC_ChangeOverTempHystHeat | 3 | Offset subtracted from the reference temperature when heating. | R | 3 | 147 | Holding | RW | 405135 | 5134 | I16SO | 10 | 0
RC_ChangeOverTempHystCool | 4 | Offset added to the reference temperature when cooling. | R | 3 | 150 | Holding | RW | 405136 | 5135 | I16SO | 10 | 0
RC_ChangeOverValveTime | 0 | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. | I | 3 | 153 | Holding | RW | 405137 | 5136 | I16
RC_ChangeOverVAVSelect | 0 | Type of detection to control change-over VAV. | X | 3 | 155 | Holding | RW | 405138 | 5137 | U8 |  |  | multi_state_value | 10423 |  | X
RC_ChangeOverVAVTemperature | 22 | The reference temperature to use in simple mode, in advanced mode the room temperature is used | R | 3 | 156 | Holding | RW | 405139 | 5138 | I16SO | 10 | 0
RC_ChangeOverVAVTempHystHeat | 3 | Offset added to the reference temperature when switching to heat mode. | R | 3 | 159 | Holding | RW | 405140 | 5139 | I16SO | 10 | 0
RC_ChangeOverVAVTempHystCool | 4 | Offset subtracted from the reference temperature when switching to cool mode. | R | 3 | 162 | Holding | RW | 405141 | 5140 | I16SO | 10 | 0
RC_ChangeOverVAVValveTime | 0 | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. | I | 3 | 165 | Holding | RW | 405142 | 5141 | I16
RC_SixWayValveCenterPoint | 5 | Voltage applied to 6 way valve for center point, closed both sequences | R | 3 | 167 | Holding | RW | 405143 | 5142 | I16SO | 10 | 0
RC_SixWayValveCenterPointHyst | 2 | Center point Hysteresis | X | 3 | 170 | Holding | RW | 405144 | 5143 | U8
RC_SixWayValveFirstSeqStartOpen | 3.3 | Voltage applied to 6 way valve to start open at sequence 1 | R | 3 | 171 | Holding | RW | 405145 | 5144 | I16SO | 10 | 0
RC_SixWayValveFirstSeqFullyOpen | 0 | Voltage applied to 6 way valve for fully open at sequence 1 | R | 3 | 174 | Holding | RW | 405146 | 5145 | I16SO | 10 | 0
RC_SixWayValveSecondSeqStartOpen | 6.7 | Voltage applied to 6 way valve to start open at sequence 2 | R | 3 | 177 | Holding | RW | 405147 | 5146 | I16SO | 10 | 0
RC_SixWayValveSecondSeqFullyOpen | 10 | Voltage applied to 6 way valve for fully open at sequence 2 | R | 3 | 180 | Holding | RW | 405148 | 5147 | I16SO | 10 | 0
RC_SixWayValveSequenceOrder | 1 | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence | L | 3 | 183 | Coil | RW | 005012 | 5011 | LOGIC
RC_RoomSetpointHeatOff | 8 | Heating setpoint in Off state (frost protection). | R | 3 | 184 | Holding | RW | 405149 | 5148 | I16SO | 10 | 0 | analog_value | 10331 | degrees_celsius | X
RC_RoomSetpointHeatUnoccupied | 15 | Heating setpoint in Unoccupied state. | R | 3 | 187 | Holding | RW | 405150 | 5149 | I16SO | 10 | 0 | analog_value | 10341 | degrees_celsius | X
RC_RoomSetpointHeatStandby | 19 | Heating setpoint in Standby state. | R | 3 | 190 | Holding | RW | 405151 | 5150 | I16SO | 10 | 0 | analog_value | 10351 | degrees_celsius | X
RC_RoomSetpointHeatOccupied | 22 | Heating setpoint in Occupied state. | R | 3 | 193 | Holding | RW | 405152 | 5151 | I16SO | 10 | 0 | analog_value | 10361 | degrees_celsius | X
RC_RoomSetpointCoolUnoccupied | 30 | Cooling setpoint in Unoccupied state. | R | 3 | 196 | Holding | RW | 405153 | 5152 | I16SO | 10 | 0 | analog_value | 10371 | degrees_celsius | X
RC_RoomSetpointCoolStandby | 27 | Cooling setpoint in Standby state. | R | 3 | 199 | Holding | RW | 405154 | 5153 | I16SO | 10 | 0 | analog_value | 10381 | degrees_celsius | X
RC_RoomSetpointCoolOccupied | 24 | Cooling setpoint in Occupied state. | R | 3 | 202 | Holding | RW | 405155 | 5154 | I16SO | 10 | 0 | analog_value | 10391 | degrees_celsius | X
RC_RoomSetpointOffset | 0 | Setpoint offset. Effective in Standby state or higher. | R | 3 | 205 | Holding | RW | 405156 | 5155 | I16SO | 10 | 0 | analog_value | 10401 | degrees_celsius | X
RC_RoomSetpointOffsetMaxPos | 3 | Maximum positive setpoint offset. | R | 3 | 208 | Holding | RW | 405157 | 5156 | I16SO | 10 | 0 | analog_value | 10411 | degrees_celsius | X
RC_RoomSetpointOffsetMaxNeg | 3 | Maximum negative setpoint offset. | R | 3 | 211 | Holding | RW | 405158 | 5157 | I16SO | 10 | 0 | analog_value | 10421 | degrees_celsius | X
RC_RoomPIDPband | 10 | P-band for room PID controller | R | 3 | 214 | Holding | RW | 405159 | 5158 | I16SO | 10 | 0 | analog_value | 10431 | degrees_celsius | X
RC_RoomPIDItime | 300 | I-time for room PID controller | R | 3 | 217 | Holding | RW | 405160 | 5159 | I16SO | 1 | 0 | analog_value | 10441 | seconds | X
RC_ExtraZoneControlFunction | 0 | Extra Zone function | X | 3 | 220 | Holding | RW | 405161 | 5160 | U8
RC_ExtraZoneSetpoint | 22 | Setpoint for Extra Zone | R | 3 | 221 | Holding | RW | 405162 | 5161 | I16SO | 10 | 0 | analog_value | 10451 | degrees_celsius | X
RC_ExtraZoneOutputMax | 100 | Maximum output for Extra Zone | X | 3 | 224 | Holding | RW | 405163 | 5162 | U8
RC_ExtraZoneOutputMin | 0 | Minimum output for Extra Zone | X | 3 | 225 | Holding | RW | 405164 | 5163 | U8
RC_ExtraZonePIDPband | 10 | P-band for Extra Zone PID controller | R | 3 | 226 | Holding | RW | 405165 | 5164 | I16SO | 10 | 0 | analog_value | 10461 | degrees_celsius | X
RC_ExtraZonePIDItime | 300 | I-time for Extra Zone PID controller | R | 3 | 229 | Holding | RW | 405166 | 5165 | I16SO | 1 | 0 | analog_value | 10471 | seconds | X
RC_ExtraZoneMinControllerState | 0 | Disable Extra Zone control below this controller state | X | 3 | 232 | Holding | RW | 405167 | 5166 | U8
RC_ExtraZoneDisableIfWrongMode | 1 | Disable Extra Zone if mode differs from room PID mode | L | 3 | 233 | Coil | RW | 005013 | 5012 | LOGIC
RC_CO2Setpoint | 600 | Setpoint for CO2 control | R | 3 | 234 | Holding | RW | 405168 | 5167 | I16SO | 10 | 0 | analog_value | 10481 | parts_per_million | X
RC_CO2PIDPband | 300 | P-band for CO2 PID controller | R | 3 | 237 | Holding | RW | 405169 | 5168 | I16SO | 10 | 0 | analog_value | 10491 | parts_per_million | X
RC_CO2PIDItime | 100 | I-time for CO2 PID controller | R | 3 | 240 | Holding | RW | 405170 | 5169 | I16SO | 1 | 0 | analog_value | 10501 | seconds | X
RC_HumiditySetpoint | 70 | Setpoint Humidity control | R | 3 | 243 | Holding | RW | 405171 | 5170 | I16SO | 10 | 0 | analog_value | 10511 | percent_relative_humidity | X
RC_HumidityPIDPband | 10 | P-band for Humidity PID controller | R | 3 | 246 | Holding | RW | 405172 | 5171 | I16SO | 10 | 0 | analog_value | 10521 | percent_relative_humidity | X
RC_HumidityPIDItime | 300 | I-time for Humidity PID controller | R | 3 | 249 | Holding | RW | 405173 | 5172 | I16SO | 1 | 0 | analog_value | 10531 | seconds | X
RC_AirflowSetpoint | 0 | Setpoint for Airflow control | R | 3 | 252 | Holding | RW | 405174 | 5173 | I16SO | 10 | 0
RC_AirflowPIDPband | 10 | P-band for Airflow PID controller | R | 3 | 255 | Holding | RW | 405175 | 5174 | I16SO | 10 | 0
RC_AirflowPIDItime | 300 | I-time for Airflow PID controller | R | 3 | 258 | Holding | RW | 405176 | 5175 | I16SO | 1 | 0
RC_SupplyAirFunction | 2 | Function of supply air limitation | X | 3 | 261 | Holding | RW | 405177 | 5176 | U8
RC_SupplyAirCascadeFactor | 3 | Conversion factor for cascade PI parameters | R | 3 | 262 | Holding | RW | 405178 | 5177 | I16SO | 10 | 0 | analog_value | 10541 |  | X
RC_SupplyAirHeatMax | 35 | Max supply air temperature when heating | R | 3 | 265 | Holding | RW | 405179 | 5178 | I16SO | 10 | 0 | analog_value | 10551 | degrees_celsius | X
RC_SupplyAirHeatMin | 24 | Min supply air temperature when heating | R | 3 | 268 | Holding | RW | 405180 | 5179 | I16SO | 10 | 0 | analog_value | 10561 | degrees_celsius | X
RC_SupplyAirCoolMax | 24 | Max supply air temperature when cooling | R | 3 | 271 | Holding | RW | 405181 | 5180 | I16SO | 10 | 0 | analog_value | 10571 | degrees_celsius | X
RC_SupplyAirCoolMin | 12 | Min supply air temperature when cooling | R | 3 | 274 | Holding | RW | 405182 | 5181 | I16SO | 10 | 0 | analog_value | 10581 | degrees_celsius | X
RC_SupplyAirFrostProtect | 8 | Min supply air temperature in frost protect | R | 3 | 277 | Holding | RW | 405183 | 5182 | I16SO | 10 | 0 | analog_value | 10591 | degrees_celsius | X
RC_FanControlMode | 3 | Select fan control mode | X | 3 | 280 | Holding | RW | 405184 | 5183 | U8
RC_FanSelect | 4 | Fan speed setting | X | 3 | 281 | Holding | RW | 405185 | 5184 | U8 |  |  | multi_state_value | 10031
RC_FanCO2Control | 0 | Fan is controlled by CO2 output | L | 3 | 282 | Coil | RW | 005014 | 5013 | LOGIC
RC_FanSpeed1Start | 20 | Output level for fan speed 1 | X | 3 | 284 | Holding | RW | 405186 | 5185 | U8
RC_FanSpeed2Start | 60 | Output level for fan speed 2 | X | 3 | 285 | Holding | RW | 405187 | 5186 | U8
RC_FanSpeed3Start | 100 | Output level for fan speed 3 | X | 3 | 286 | Holding | RW | 405188 | 5187 | U8
RC_FanSpeedMax | 3 | Max fan speed | X | 3 | 287 | Holding | RW | 405189 | 5188 | U8
RC_FanSpeedHyst | 5 | Hysteresis for fan speed outputs | X | 3 | 288 | Holding | RW | 405190 | 5189 | U8
RC_FanSpeedMin | 0 | Fan never stops in auto mode | L | 3 | 289 | Coil | RW | 005016 | 5015 | LOGIC
RC_FanMouldProtect | 0 | Mould protect active. Fan never stops regardless of other settings | L | 3 | 290 | Coil | RW | 005017 | 5016 | LOGIC
RC_FanPreventManualControl | 0 | Prevent manual fan speed setting | L | 3 | 291 | Coil | RW | 005018 | 5017 | LOGIC
RC_FanKickStartTime | 0 | Fan kick start time | X | 3 | 292 | Holding | RW | 405005 | 5004 | U8
RC_FanForcedVentilation | 0 | Fan runs at RC_ECFanSpeedForced when forced ventilation is active | L | 3 | 293 | Coil | RW | 005019 | 5018 | LOGIC
RC_FanBoostMode | 0 | Fan start boost heat cool select. 0=heat, 1=cool, 2=both | X | 3 | 294 | Holding | RW | 405191 | 5190 | U8
RC_FanBoostRunTime | 120 | Fan boost run time. 0 = Not active | I | 3 | 295 | Holding | RW | 405192 | 5191 | I16
RC_FanAfterblowMinSpeed | 0 | Fan afterblow min speed | X | 3 | 297 | Holding | RW | 405193 | 5192 | U8
RC_FanAfterblowTime | 0 | Fan afterblow run time. 0 = Not active | I | 3 | 298 | Holding | RW | 405194 | 5193 | I16
RC_ECFanManualSpeed1 | 20 | EC fan speed for manual speed 1 | X | 3 | 300 | Holding | RW | 405195 | 5194 | U8
RC_ECFanManualSpeed2 | 60 | EC fan speed for manual speed 2 | X | 3 | 301 | Holding | RW | 405196 | 5195 | U8
RC_ECFanManualSpeed3 | 100 | EC fan speed for manual speed 3 | X | 3 | 302 | Holding | RW | 405197 | 5196 | U8
RC_ECFanSpeedForced | 100 | Forced ventilation EC fan speed | X | 3 | 303 | Holding | RW | 405198 | 5197 | U8
RC_ECFanSpeedMax | 100 | Max EC fan speed in % | X | 3 | 304 | Holding | RW | 405199 | 5198 | U8
RC_ECFanSpeedMin | 10 | Min EC fan speed in % | X | 3 | 305 | Holding | RW | 405200 | 5199 | U8
RC_ECFanSpeedStartLimit | 15 | Min EC fan speed in % | X | 3 | 306 | Holding | RW | 405201 | 5200 | U8
RC_ForcedVentMode | 0 | Forced ventilation function | X | 3 | 307 | Holding | RW | 405202 | 5201 | U8
RC_ForcedVentStartLimit | 100 | Forced ventilation start limit | X | 3 | 308 | Holding | RW | 405203 | 5202 | U8
RC_ControllerStateDefault | 3 | The default state when nothing else is controlling the state. | X | 3 | 309 | Holding | RW | 405204 | 5203 | U8 |  |  | multi_state_value | 10041 |  | X
RC_RemoteControllerState | 5 | Sets the state directly via communication. | X | 3 | 310 | Holding | RW | 405205 | 5204 | U8 |  |  | multi_state_value | 10051 |  | X
RC_ControllerStatePresence | 3 | The state to enter when presence is detected. | X | 3 | 311 | Holding | RW | 405206 | 5205 | U8 |  |  | multi_state_value | 10061 |  | X
RC_ControllerStateShutdown | 1 | The state to enter when shutdown mode is set. | X | 3 | 312 | Holding | RW | 405207 | 5206 | U8 |  |  | multi_state_value | 10071 |  | X
RC_ControllerStateFail | 2 | State to set during communication faults | X | 3 | 313 | Holding | RW | 405208 | 5207 | U8 |  |  | multi_state_value | 10081 |  | X
RC_ControllerStateSetBypass | 0 | Set controller in Bypass state | L | 3 | 314 | Coil | RW | 005020 | 5019 | LOGIC
RC_ControllerStateSetShutdown | 0 | Set controller in the state indicated by RC_ControllerStateShutdown | L | 3 | 315 | Coil | RW | 005021 | 5020 | LOGIC
RC_BypassTime | 120 | Bypass time (minutes) | I | 3 | 316 | Holding | RW | 405209 | 5208 | I16 |  |  | analog_value | 10601 | minutes | X
RC_RoomTempRemote | 22 | Remote setting of room temperature | R | 3 | 318 | Holding | RW | 405210 | 5209 | I16SO | 10 | 0 | analog_value | 10611 | degrees_celsius | X
RC_CO2LevelRemote | 400 | Remote setting of room CO2 level | R | 3 | 321 | Holding | RW | 405211 | 5210 | I16SO | 10 | 0 | analog_value | 10621 | parts_per_million | X
RC_AirFlowRemote | 0 | Remote setting of air flow | R | 3 | 324 | Holding | RW | 405212 | 5211 | I16SO | 10 | 0 | analog_value | 10631 | liters_per_second | X
RC_ChangeOverTempRemote | 22 | Remote setting of changeover temperature | R | 3 | 327 | Holding | RW | 405213 | 5212 | I16SO | 10 | 0 | analog_value | 10641 | degrees_celsius | X
RC_ChangeOverVAVTempRemote | 22 | Remote setting of changeover VAV temperature | R | 3 | 330 | Holding | RW | 405214 | 5213 | I16SO | 10 | 0 | analog_value | 10651 | degrees_celsius | X
RC_ExtraZoneTempRemote | 22 | Remote setting of extra zone temperature | R | 3 | 333 | Holding | RW | 405215 | 5214 | I16SO | 10 | 0 | analog_value | 10661 | degrees_celsius | X
RC_SupplyAirTempRemote | 22 | Remote setting of supply air temperature | R | 3 | 336 | Holding | RW | 405216 | 5215 | I16SO | 10 | 0 | analog_value | 10671 | degrees_celsius | X
RC_HumidityRemote | 50 | Remote setting of relative humidity | R | 3 | 339 | Holding | RW | 405217 | 5216 | I16SO | 10 | 0 | analog_value | 10681 | percent_relative_humidity | X
RC_VOCRemote | 100 | Remote setting of VOC index | R | 3 | 342 | Holding | RW | 405218 | 5217 | I16SO | 10 | 0 | analog_value | 10691 |  | X
RC_RoomTempRemoteSelect | 0 | Enable remote setting of room temperature | L | 3 | 345 | Coil | RW | 005022 | 5021 | LOGIC |  |  | binary_value | 10321 |  | X
RC_CO2LevelRemoteSelect | 0 | Enable remote setting of room CO2 level | L | 3 | 346 | Coil | RW | 005023 | 5022 | LOGIC |  |  | binary_value | 10331 |  | X
RC_AirFlowRemoteSelect | 0 | Enable remote setting of air flow | L | 3 | 347 | Coil | RW | 005024 | 5023 | LOGIC |  |  | binary_value | 10341 |  | X
RC_ChangeOverTempRemoteSelect | 0 | Enable remote setting of changeover temperature | L | 3 | 348 | Coil | RW | 005025 | 5024 | LOGIC |  |  | binary_value | 10351 |  | X
RC_ChangeOverVAVTempRemoteSelect | 0 | Enable remote setting of changeover VAV temperature | L | 3 | 349 | Coil | RW | 005026 | 5025 | LOGIC |  |  | binary_value | 10361 |  | X
RC_ExtraZoneTempRemoteSelect | 0 | Enable remote setting of extra zone temperature | L | 3 | 350 | Coil | RW | 005027 | 5026 | LOGIC |  |  | binary_value | 10371 |  | X
RC_SupplyAirTempRemoteSelect | 0 | Enable remote setting of supply air temperature | L | 3 | 351 | Coil | RW | 005028 | 5027 | LOGIC |  |  | binary_value | 10381 |  | X
RC_HumidityRemoteSelect | 0 | Enable remote setting of relative humidity | L | 3 | 352 | Coil | RW | 005029 | 5028 | LOGIC |  |  | binary_value | 10391 |  | X
RC_VOCRemoteSelect | 0 | Enable remote setting of VOC index | L | 3 | 353 | Coil | RW | 005030 | 5029 | LOGIC |  |  | binary_value | 10401 |  | X
RC_DIPresenceRemote | 0 | Remote setting of presence digital input | L | 3 | 354 | Coil | RW | 005031 | 5030 | LOGIC |  |  | binary_value | 10411 |  | X
RC_DIOpenWindowRemote | 0 | Remote setting of window contact digital input | L | 3 | 355 | Coil | RW | 005032 | 5031 | LOGIC |  |  | binary_value | 10421 |  | X
RC_DIChangeoverRemote | 0 | Remote setting of change over digital input | L | 3 | 356 | Coil | RW | 005033 | 5032 | LOGIC |  |  | binary_value | 10431 |  | X
RC_DIChangeoverVAVRemote | 0 | Remote setting of change over VAV digital input | L | 3 | 357 | Coil | RW | 005034 | 5033 | LOGIC |  |  | binary_value | 10441 |  | X
RC_DICondensationRemote | 0 | Remote setting of condensation digital input | L | 3 | 358 | Coil | RW | 005035 | 5034 | LOGIC |  |  | binary_value | 10451 |  | X
RC_RoomHeat1OutputManual | 0 | Manual setting of RoomHeat1Output | X | 3 | 359 | Holding | RW | 405219 | 5218 | U8 |  |  | analog_value | 10701 | percent | X
RC_RoomCool1OutputManual | 0 | Manual setting of RoomCool1Output | X | 3 | 360 | Holding | RW | 405220 | 5219 | U8 |  |  | analog_value | 10711 | percent | X
RC_RoomVAV1OutputManual | 0 | Manual setting of RoomVAV1Output | X | 3 | 361 | Holding | RW | 405221 | 5220 | U8 |  |  | analog_value | 10721 | percent | X
RC_RoomHeat2OutputManual | 0 | Manual setting of RoomHeat2Output | X | 3 | 362 | Holding | RW | 405222 | 5221 | U8 |  |  | analog_value | 10731 | percent | X
RC_RoomCool2OutputManual | 0 | Manual setting of RoomCool2Output | X | 3 | 363 | Holding | RW | 405223 | 5222 | U8 |  |  | analog_value | 10741 | percent | X
RC_RoomVAV2OutputManual | 0 | Manual setting of RoomVAV2Output | X | 3 | 364 | Holding | RW | 405224 | 5223 | U8 |  |  | analog_value | 10751 | percent | X
RC_RoomChangeOverOutputManual | 0 | Manual setting of RoomChangeOverOutput | X | 3 | 365 | Holding | RW | 405225 | 5224 | U8 |  |  | analog_value | 10761 | percent | X
RC_Room6WayValveOutputManual | 0 | Manual setting of Room6WayValveOutput | X | 3 | 366 | Holding | RW | 405226 | 5225 | U8 |  |  | analog_value | 10771 | percent | X
RC_RoomChangeOverVAVOutputManual | 0 | Manual setting of RoomChangeOverVAVOutput | X | 3 | 367 | Holding | RW | 405227 | 5226 | U8 |  |  | analog_value | 10781 | percent | X
RC_ExtraZoneOutputManual | 0 | Manual setting of ExtraZoneOutput | X | 3 | 368 | Holding | RW | 405228 | 5227 | U8 |  |  | analog_value | 10791 | percent | X
RC_ECFanSpeedManual | 0 | Manual setting of ECFanSpeed | X | 3 | 369 | Holding | RW | 405229 | 5228 | U8 |  |  | analog_value | 10801 |  | X
RC_CO2ControlManual | 0 | Manual setting of CO2Control | X | 3 | 370 | Holding | RW | 405230 | 5229 | U8 |  |  | analog_value | 10811 | percent | X
RC_HumidifyOutputManual | 0 | Manual setting of HumidifyOutput | X | 3 | 371 | Holding | RW | 405231 | 5230 | U8 |  |  | analog_value | 10821 |  | X
RC_DehumidifyOutputManual | 0 | Manual setting of DehumidifyOutput | X | 3 | 372 | Holding | RW | 405232 | 5231 | U8 |  |  | analog_value | 10831 | percent | X
RC_AirflowControlManual | 0 | Manual setting of AirflowControl | X | 3 | 373 | Holding | RW | 405233 | 5232 | U8
RC_RoomHeat1OutputManSelect | 2 | Manual/auto select for RoomHeat1Output | X | 3 | 374 | Holding | RW | 405234 | 5233 | U8 |  |  | multi_state_value | 10091 |  | X
RC_RoomCool1OutputManSelect | 2 | Manual/auto select for RoomCool1Output | X | 3 | 375 | Holding | RW | 405235 | 5234 | U8 |  |  | multi_state_value | 10101 |  | X
RC_RoomVAV1OutputManSelect | 2 | Manual/auto select for RoomVAV1Output | X | 3 | 376 | Holding | RW | 405236 | 5235 | U8 |  |  | multi_state_value | 10111 |  | X
RC_RoomHeat2OutputManSelect | 2 | Manual/auto select for RoomHeat2Output | X | 3 | 377 | Holding | RW | 405237 | 5236 | U8 |  |  | multi_state_value | 10121 |  | X
RC_RoomCool2OutputManSelect | 2 | Manual/auto select for RoomCool2Output | X | 3 | 378 | Holding | RW | 405238 | 5237 | U8 |  |  | multi_state_value | 10131 |  | X
RC_RoomVAV2OutputManSelect | 2 | Manual/auto select for RoomVAV2Output | X | 3 | 379 | Holding | RW | 405239 | 5238 | U8 |  |  | multi_state_value | 10141 |  | X
RC_RoomChangeOverOutputManSelect | 2 | Manual/auto select for RoomChangeOverOutput | X | 3 | 380 | Holding | RW | 405240 | 5239 | U8
RC_Room6WayValveOutputManSelect | 2 | Manual/auto select for Room6WayValveOutput | X | 3 | 381 | Holding | RW | 405241 | 5240 | U8 |  |  | multi_state_value | 10151 |  | X
RC_RoomChangeOverVAVOutputManSelect | 2 | Manual/auto select for RoomChangeOverVAVOutput | X | 3 | 382 | Holding | RW | 405242 | 5241 | U8 |  |  | multi_state_value | 10161 |  | X
RC_ExtraZoneOutputManSelect | 2 | Manual/auto select for ExtraZoneOutput | X | 3 | 383 | Holding | RW | 405243 | 5242 | U8 |  |  | multi_state_value | 10171 |  | X
RC_ECFanSpeedManSelect | 2 | Manual/auto select for ECFanSpeed | X | 3 | 384 | Holding | RW | 405244 | 5243 | U8 |  |  | multi_state_value | 10181 |  | X
RC_CO2ControlManSelect | 2 | Manual/auto select for CO2Control | X | 3 | 385 | Holding | RW | 405245 | 5244 | U8 |  |  | multi_state_value | 10191 |  | X
RC_HumidifyOutputManSelect | 2 | Manual/auto select for HumidifyOutput | X | 3 | 386 | Holding | RW | 405246 | 5245 | U8 |  |  | multi_state_value | 10201 |  | X
RC_DehumidifyOutputManSelect | 2 | Manual/auto select for DehumidifyOutput | X | 3 | 387 | Holding | RW | 405247 | 5246 | U8 |  |  | multi_state_value | 10211 |  | X
RC_AirflowControlManSelect | 2 | Manual/auto select for AirflowControl | X | 3 | 388 | Holding | RW | 405248 | 5247 | U8
RC_PresenceDelayOn | 0 | Delay for presence on (min) | I | 3 | 389 | Holding | RW | 405249 | 5248 | I16
RC_PresenceDelayOff | 10 | Delay for presence off (min) | I | 3 | 391 | Holding | RW | 405250 | 5249 | I16
RC_PresenceCO2Enable | 0 | Enable CO2 presence detection | L | 3 | 393 | Coil | RW | 005036 | 5035 | LOGIC
RC_PresenceCO2Limit | 800 | CO2 presence limit | R | 3 | 394 | Holding | RW | 405251 | 5250 | I16SO | 10 | 0
RC_PresenceCO2Hyst | 160 | CO2 presence limit hysteresis | R | 3 | 397 | Holding | RW | 405252 | 5251 | I16SO | 10 | 0
RC_ValveExerciseFunction | 0 | Valve exercise function | X | 3 | 400 | Holding | RW | 405253 | 5252 | U8
RC_ValveExerciseIntervalHeat1 | 23 | Heat valve 1 exercise interval (hours) | X | 3 | 401 | Holding | RW | 405254 | 5253 | U8
RC_ValveExerciseIntervalCool1 | 23 | Cool valve 1 exercise interval (hours) | X | 3 | 402 | Holding | RW | 405255 | 5254 | U8
RC_ValveExerciseIntervalHeat2 | 23 | Heat valve 2 exercise interval (hours) | X | 3 | 403 | Holding | RW | 405256 | 5255 | U8
RC_ValveExerciseIntervalCool2 | 23 | Cool valve 2 exercise interval (hours) | X | 3 | 404 | Holding | RW | 405257 | 5256 | U8
RC_ValveExerciseIntervalChangeOver | 23 | Change-over valve exercise interval (hours) | X | 3 | 405 | Holding | RW | 405258 | 5257 | U8
RC_ValveExerciseInterval6Way | 23 | 6-way valve exercise interval (hours) | X | 3 | 406 | Holding | RW | 405259 | 5258 | U8
RC_ValveRuntimeHeat1 | 120 | Heat valve 1 runtime (seconds) | I | 3 | 407 | Holding | RW | 405260 | 5259 | I16
RC_ValveRuntimeCool1 | 120 | Cool valve 1 runtime (seconds) | I | 3 | 409 | Holding | RW | 405261 | 5260 | I16
RC_ValveRuntimeHeat2 | 120 | Heat valve 2 runtime (seconds) | I | 3 | 411 | Holding | RW | 405262 | 5261 | I16
RC_ValveRuntimeCool2 | 120 | Cool valve 2 runtime (seconds) | I | 3 | 413 | Holding | RW | 405263 | 5262 | I16
RC_ValveRuntimeChangeOver | 120 | Change-over valve runtime (seconds) | I | 3 | 415 | Holding | RW | 405264 | 5263 | I16
RC_ValveRuntime6Way | 120 | 6-way valve runtime (seconds) | I | 3 | 417 | Holding | RW | 405265 | 5264 | I16
RC_AlarmRoomTempLimitHigh | 40 | High room temp alarm limit | R | 3 | 419 | Holding | RW | 405266 | 5265 | I16SO | 10 | 0 | analog_value | 10841 | degrees_celsius | X
RC_AlarmRoomTempLimitLow | 15 | Low room temp alarm limit | R | 3 | 422 | Holding | RW | 405267 | 5266 | I16SO | 10 | 0 | analog_value | 10851 | degrees_celsius | X
RC_AlarmCO2LimitHigh | 2000 | High CO2 alarm limit | R | 3 | 425 | Holding | RW | 405268 | 5267 | I16SO | 10 | 0 | analog_value | 10861 | parts_per_million | X
RC_ResetUserSettingsAtShutdown | 0 | Reset user settings in shutdown state | L | 3 | 428 | Coil | RW | 005037 | 5036 | LOGIC
RC_DamperPositionRemote | 0 | Remote setting of damper position | R | 3 | 429 | Holding | RW | 405269 | 5268 | I16SO | 10 | 0 | analog_value | 10871 |  | X
RC_ExtractTemperaureRemote | 22 | Remote setting of extract temperature | R | 3 | 432 | Holding | RW | 405270 | 5269 | I16SO | 10 | 0 | analog_value | 10881 | degrees_celsius | X
RC_DamperPositionRemoteSelect | 0 | Enable remote setting of damper position | L | 3 | 435 | Coil | RW | 005038 | 5037 | LOGIC |  |  | binary_value | 10461 |  | X
RC_ExtractTemperaureRemoteSelect | 0 | Enable remote setting of extract temperature | L | 3 | 436 | Coil | RW | 005039 | 5038 | LOGIC |  |  | binary_value | 10471 |  | X
RC_DIPresenceRemoteSelect | 0 | Enable remote setting of presence digital input | L | 3 | 437 | Coil | RW | 005040 | 5039 | LOGIC |  |  | binary_value | 10481 |  | X
RC_DIOpenWindowRemoteSelect | 0 | Enable remote setting of window contact digital input | L | 3 | 438 | Coil | RW | 005041 | 5040 | LOGIC |  |  | binary_value | 10491 |  | X
RC_DIChangeoverRemoteSelect | 0 | Enable remote setting of change over digital input | L | 3 | 439 | Coil | RW | 005042 | 5041 | LOGIC |  |  | binary_value | 10501 |  | X
RC_DIChangeoverVAVRemoteSelect | 0 | Enable remote setting of change over VAV digital input | L | 3 | 440 | Coil | RW | 005043 | 5042 | LOGIC |  |  | binary_value | 10511 |  | X
RC_DICondensationRemoteSelect | 0 | Enable remote setting of condensation digital input | L | 3 | 441 | Coil | RW | 005044 | 5043 | LOGIC |  |  | binary_value | 10521 |  | X
RC_DisplayViewMode | 0 | Select value to be shown in the display | X | 3 | 442 | Holding | RW | 405271 | 5270 | U8 |  |  | multi_state_value | 10221 |  | X
RC_DisplaySetpointMode | 0 | Select setpoint display at setpoint adjustment | X | 3 | 443 | Holding | RW | 405272 | 5271 | U8 |  |  | multi_state_value | 10231 |  | X
RC_RoomHeat1OutputManSelectDO | 2 | Manual/auto select Heat1 output digital | X | 3 | 444 | Holding | RW | 405273 | 5272 | U8 |  |  | multi_state_value | 10241 |  | X
RC_RoomCool1OutputManSelectDO | 2 | Manual/auto select Cool1 output digital | X | 3 | 445 | Holding | RW | 405274 | 5273 | U8 |  |  | multi_state_value | 10251 |  | X
RC_RoomVAV1OutputManSelectDO | 2 | Manual/auto select VAV1 output digital | X | 3 | 446 | Holding | RW | 405275 | 5274 | U8 |  |  | multi_state_value | 10261 |  | X
RC_RoomHeat2OutputManSelectDO | 2 | Manual/auto select Heat2 output digital | X | 3 | 447 | Holding | RW | 405276 | 5275 | U8 |  |  | multi_state_value | 10271 |  | X
RC_RoomCool2OutputManSelectDO | 2 | Manual/auto select Cool2 output digital | X | 3 | 448 | Holding | RW | 405277 | 5276 | U8 |  |  | multi_state_value | 10281 |  | X
RC_RoomVAV2OutputManSelectDO | 2 | Manual/auto select VAV2 output digital | X | 3 | 449 | Holding | RW | 405278 | 5277 | U8 |  |  | multi_state_value | 10291 |  | X
RC_RoomChangeOverOutputManSelectDO | 2 | Manual/auto select Change over output digital | X | 3 | 450 | Holding | RW | 405279 | 5278 | U8 |  |  | multi_state_value | 10301 |  | X
RC_Room6WayValveOutputManSelectDO | 2 | Manual/auto select 6-way valve output digital | X | 3 | 451 | Holding | RW | 405280 | 5279 | U8 |  |  | multi_state_value | 10311 |  | X
RC_RoomChangeOverVAVOutputManSelectDO | 2 | Manual/auto select Change over VAV output digital | X | 3 | 452 | Holding | RW | 405281 | 5280 | U8 |  |  | multi_state_value | 10321 |  | X
RC_ExtraZoneOutputManSelectDO | 2 | Manual/auto select Extra Zone output digital | X | 3 | 453 | Holding | RW | 405282 | 5281 | U8 |  |  | multi_state_value | 10331 |  | X
RC_CO2ControlManSelectDO | 2 | Manual/auto select CO2 control digital out | X | 3 | 454 | Holding | RW | 405283 | 5282 | U8 |  |  | multi_state_value | 10341 |  | X
RC_HumidifyOutputManSelectDO | 2 | Manual/auto select Humidify digital out | X | 3 | 455 | Holding | RW | 405284 | 5283 | U8 |  |  | multi_state_value | 10351 |  | X
RC_DehumidifyOutputManSelectDO | 2 | Manual/auto select Dehumidify digital out | X | 3 | 456 | Holding | RW | 405285 | 5284 | U8 |  |  | multi_state_value | 10361 |  | X
RC_AirflowControlManSelectDO | 2 | Manual/auto select Airflow control digital out | X | 3 | 457 | Holding | RW | 405286 | 5285 | U8
RC_ForcedVentilationManSelectDO | 2 | Manual/auto select Forced Ventilation digital out | X | 3 | 458 | Holding | RW | 405287 | 5286 | U8 |  |  | multi_state_value | 10371 |  | X
RC_LightControlManSelectDO | 2 | Manual/auto select Light control digital out | X | 3 | 459 | Holding | RW | 405288 | 5287 | U8
RC_SumAlarmManSelectDO | 2 | Manual/auto select Sum Alarm | X | 3 | 460 | Holding | RW | 405289 | 5288 | U8 |  |  | multi_state_value | 10381 |  | X
RC_ExtraZoneActiveManSelectDO | 2 | Manual/auto select Extra Zone active digital out | X | 3 | 461 | Holding | RW | 405290 | 5289 | U8 |  |  | multi_state_value | 10391 |  | X
RC_CO2_0V | 0 | CO2 at 0 Volt input | R | 3 | 462 | Holding | RW | 405291 | 5290 | I16SO | 1 | 0
RC_CO2_10V | 2000 | CO2 at 10 Volt input | R | 3 | 465 | Holding | RW | 405292 | 5291 | I16SO | 1 | 0
RC_RH_0V | 0 | RH at 0 Volt input | R | 3 | 468 | Holding | RW | 405293 | 5292 | I16SO | 10 | 0
RC_RH_10V | 100 | RH at 10 Volt input | R | 3 | 471 | Holding | RW | 405294 | 5293 | I16SO | 10 | 0
RC_RoomTemp_0V | 0 | Room temperature at 0 Volt input | R | 3 | 474 | Holding | RW | 405295 | 5294 | I16SO | 10 | 0
RC_RoomTemp_10V | 100 | Room temperature at 10 Volt input | R | 3 | 477 | Holding | RW | 405296 | 5295 | I16SO | 10 | 0
RC_Flow_0V | 0 | Air flow at 0 Volt input | R | 3 | 480 | Holding | RW | 405297 | 5296 | I16SO | 10 | 0
RC_Flow_10V | 100 | Air flow at 10 Volt input | R | 3 | 483 | Holding | RW | 405298 | 5297 | I16SO | 10 | 0
RC_VOC_0V | 0 | VOC index at 0 Volt input | R | 3 | 486 | Holding | RW | 405299 | 5298 | I16SO | 10 | 0
RC_VOC_10V | 500 | VOC index at 10 Volt input | R | 3 | 489 | Holding | RW | 405300 | 5299 | I16SO | 10 | 0
RC_CO2FilterTime | 5 | CO2 filter time (0 to 17200 seconds) | I | 3 | 492 | Holding | RW | 405301 | 5300 | I16
RC_RHFilterTime | 5 | RH filter time (0 to 17200 seconds) | I | 3 | 494 | Holding | RW | 405302 | 5301 | I16
RC_TempFilterTime | 5 | Temperature filter time (0 to 17200 seconds) | I | 3 | 496 | Holding | RW | 405303 | 5302 | I16
RC_FlowFilterTime | 5 | Air flow filter time (0 to 17200 seconds) | I | 3 | 498 | Holding | RW | 405304 | 5303 | I16
RC_VOCFilterTime | 5 | VOC index filter time (0 to 17200 seconds) | I | 3 | 500 | Holding | RW | 405305 | 5304 | I16
RC_CO2LevelYellow | 800 | CO2 level for yellow led | R | 3 | 502 | Holding | RW | 405306 | 5305 | I16SO | 1 | 0 | analog_value | 10891 | parts_per_million | X
RC_CO2LevelRed | 1000 | CO2 level for red led | R | 3 | 505 | Holding | RW | 405307 | 5306 | I16SO | 1 | 0 | analog_value | 10901 | parts_per_million | X
RC_CO2SetIndication | 0 | Enable/disable CO2 led indication | X | 3 | 508 | Holding | RW | 405308 | 5307 | U8
RC_FanBoostShortTime | 10 | Fan boost short run time | I | 3 | 509 | Holding | RW | 405309 | 5308 | I16
RC_FanBoostPBand | 5 | Fan boost P band | R | 3 | 511 | Holding | RW | 405310 | 5309 | I16SO | 1 | 0
RC_CO2Step | 1 | Min step for CO2 value | R | 3 | 514 | Holding | RW | 405311 | 5310 | I16SO | 1 | 0
RC_TemperatureCO2 | 0 | Alternate temperature/CO2 display | L | 3 | 517 | Coil | RW | 005045 | 5044 | LOGIC
RC_ForcedApplicationOff | 0 | Set to 1 to disable all regulator functions | L | 3 | 518 | Coil | RW | 005046 | 5045 | LOGIC
RC_VOCSetpoint | 100 | Setpoint for VOC control | R | 3 | 519 | Holding | RW | 405312 | 5311 | I16SO | 10 | 0 | analog_value | 10911 | no_units | X
RC_VOCPIDPband | 50 | P-band for VOC PID controller | R | 3 | 522 | Holding | RW | 405313 | 5312 | I16SO | 10 | 0 | analog_value | 10921 | no_units | X
RC_VOCPIDItime | 300 | I-time for VOC PID controller | R | 3 | 525 | Holding | RW | 405314 | 5313 | I16SO | 1 | 0 | analog_value | 10931 | seconds | X
RC_VOCControlManual | 0 | Manual setting of VOCControl | X | 3 | 528 | Holding | RW | 405315 | 5314 | U8 |  |  | analog_value | 10941 | percent | X
RC_VOCControlManSelect | 2 | Manual/auto select for VOCControl | X | 3 | 529 | Holding | RW | 405316 | 5315 | U8 |  |  | multi_state_value | 10401 |  | X
RC_VOCControlManSelectDO | 2 | Manual/auto select VOC control digital out | X | 3 | 530 | Holding | RW | 405317 | 5316 | U8 |  |  | multi_state_value | 10411 |  | X
RC_ControllerStateWindow | 0 | The state to enter when the window is opened | X | 3 | 531 | Holding | RW | 405318 | 5317 | U8 |  |  | multi_state_value | 10421 |  | X
RC_DIAlarmRemote | 0 | Remote setting of alarm digital input | L | 3 | 532 | Coil | RW | 005047 | 5046 | LOGIC
RC_DIAlarmRemoteSelect | 0 | Enable remote setting of alarm digital input | L | 3 | 533 | Coil | RW | 005048 | 5047 | LOGIC
RC_VAV2OutputMaxHeat | 0 | VAV2 maximum output when the controller is in heating mode. | X | 3 | 534 | Holding | RW | 405319 | 5318 | U8
RC_PIDPresence | 1 | Use internal PID sensor for presence detection | L | 3 | 535 | Coil | RW | 005049 | 5048 | LOGIC
RC_RoomTempHeatHyst | 2 | Room temperature heating hysteresis for thermostat | R | 3 | 536 | Holding | RW | 405320 | 5319 | I16SO | 10 | 0
RC_RoomTempCoolHyst | 2 | Room temperature cooling hysteresis for thermostat | R | 3 | 539 | Holding | RW | 405321 | 5320 | I16SO | 10 | 0
RC_ExtraZoneTempHyst | 2 | Extra zone temperature hysteresis for thermostat | R | 3 | 542 | Holding | RW | 405322 | 5321 | I16SO | 10 | 0
RC_Flow_unit | 95 | BACnet unit for air flow | I | 3 | 545 | Holding | RW | 405323 | 5322 | I16
RC_Room6WayValveOutputHeatCool | 0 | Manual setting of 6-way valve heat/cool | L | 3 | 547 | Coil | RW | 005050 | 5049 | LOGIC
RC_VAVControlHumidity | 0 | VAV controlled by humidify or dehumidify output | X | 3 | 548 | Holding | RW | 405324 | 5323 | U8
RC_VAVControlVOC | 0 | VAV is controlled by VOC output | L | 3 | 549 | Coil | RW | 005051 | 5050 | LOGIC
RC_BypassExtendedRun | 0 | Enable forced ventilation extended run | L | 3 | 551 | Coil | RW | 005052 | 5051 | LOGIC
RC_FanControlHumidity | 0 | Fan is controlled by humidity output | X | 3 | 552 | Holding | RW | 405326 | 5325 | U8
RC_ChangeOverUserSelect | 2 | User controlled change-over setting | X | 3 | 553 | Holding | RW | 405327 | 5326 | U8
RC_Heat1InChangeOver | 0 | Heat1 included in change-over function | L | 3 | 554 | Coil | RW | 005053 | 5052 | LOGIC
RC_Cool1InChangeOver | 0 | Cool1 included in change-over function | L | 3 | 555 | Coil | RW | 005054 | 5053 | LOGIC
RC_VAV1InChangeOver | 0 | VAV1 included in change-over function | L | 3 | 556 | Coil | RW | 005055 | 5054 | LOGIC
RC_SixWayValveInChangeOver | 0 | 6 way valve included in change-over function | L | 3 | 557 | Coil | RW | 005056 | 5055 | LOGIC
RC_Heat2InChangeOver | 0 | Heat2 included in change-over function | L | 3 | 558 | Coil | RW | 005057 | 5056 | LOGIC
RC_Cool2InChangeOver | 0 | Cool2 included in change-over function | L | 3 | 559 | Coil | RW | 005058 | 5057 | LOGIC
RC_VAV2InChangeOver | 0 | VAV2 included in change-over function | L | 3 | 560 | Coil | RW | 005059 | 5058 | LOGIC
IoAnaIn_1_value |  | Filtered value from sensor | R | 4 | 0 | Input | R | 301001 301002 | 1000 1001 | REGx2I32SO | 100 | 0 | analog_value | 1001
IoAnaIn_1_mode | 3 | Mode for input | X | 4 | 3 | Holding | RW | 401001 | 1000 | U8
IoAnaIn_1_unit | 0 | Unit converter | X | 4 | 4 | Holding | RW | 401002 | 1001 | U8
IoAnaIn_1_min_in | -100 | Scale for input | R | 4 | 5 | Holding | RW | 401003 401004 | 1002 1003 | REGx2I32SO | 100 | 0
IoAnaIn_1_min_out | -100 | Scale for input | R | 4 | 8 | Holding | RW | 401005 401006 | 1004 1005 | REGx2I32SO | 100 | 0
IoAnaIn_1_max_in | 10000 | Scale for input | R | 4 | 11 | Holding | RW | 401007 401008 | 1006 1007 | REGx2I32SO | 100 | 0
IoAnaIn_1_max_out | 10000 | Scale for input | R | 4 | 14 | Holding | RW | 401009 401010 | 1008 1009 | REGx2I32SO | 100 | 0
IoAnaIn_1_offset | 0 | Offset for input | R | 4 | 17 | Holding | RW | 401011 | 1010 | I16SO | 100 | 0
IoAnaIn_1_prefilter |  | Unfiltered value from sensor | R | 4 | 23 | Input | R | 301003 301004 | 1002 1003 | REGx2I32SO | 100 | 0
IoAnaIn_1_raw |  | Raw value from sensor | R | 4 | 26 | Input | R | 301005 301006 | 1004 1005 | REGx2I32SO | 100 | 0
IoAnaIn_1_override | 0 | Override value | R | 4 | 29 | Holding | RW | 401014 401015 | 1013 1014 | REGx2I32SO | 100 | 0 | analog_value | 1101 |  | X
IoAnaIn_1_override_en | 0 | Set to 1 to enable override | L | 4 | 32 | Coil | RW | 001001 | 1000 | LOGIC |  |  | binary_value | 1001 |  | X
IoAnaIn_1_error |  | Flag indicating any fault for signal | L | 4 | 33 | Discrete | R | 101001 | 1000 | LOGIC
IoAnaIn_1_errorFlags | 0 | Detailed fault description | H | 4 | 34 | Holding | RW | 401016 401017 | 1015 1016 | REGx2I32
IoAnaIn_1_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 37 | Holding | RW | 401018 | 1017 | I16
IoAnaIn_1_limit | 0 | Use Max and Min values as limits, or set error if outside | L | 4 | 39 | Coil | RW | 001002 | 1001 | LOGIC
IoAnaIn_1_hyst | 0 | Hysteresis limit | R | 4 | 40 | Holding | RW | 401019 | 1018 | I16SO | 100 | 0
IoAnaIn_1_accumulate | 100 | Time in milliseconds to accumulate samples before processing | I | 4 | 43 | Holding | RW | 401020 | 1019 | I16
IoAnaIn_1_valueDigits | 2 | Number of shown digits | I | 4 | 46 | Holding | RW | 401021 | 1020 | I16
IoAnaIn_2_value |  | Filtered value from sensor | R | 4 | 50 | Input | R | 301026 301027 | 1025 1026 | REGx2I32SO | 100 | 0 | analog_value | 1002
IoAnaIn_2_mode | 9 | Mode for input | X | 4 | 53 | Holding | RW | 401026 | 1025 | U8
IoAnaIn_2_unit | 0 | Unit converter | X | 4 | 54 | Holding | RW | 401027 | 1026 | U8
IoAnaIn_2_min_in | -100 | Scale for input | R | 4 | 55 | Holding | RW | 401028 401029 | 1027 1028 | REGx2I32SO | 100 | 0
IoAnaIn_2_min_out | -100 | Scale for input | R | 4 | 58 | Holding | RW | 401030 401031 | 1029 1030 | REGx2I32SO | 100 | 0
IoAnaIn_2_max_in | 10000 | Scale for input | R | 4 | 61 | Holding | RW | 401032 401033 | 1031 1032 | REGx2I32SO | 100 | 0
IoAnaIn_2_max_out | 10000 | Scale for input | R | 4 | 64 | Holding | RW | 401034 401035 | 1033 1034 | REGx2I32SO | 100 | 0
IoAnaIn_2_offset | 0 | Offset for input | R | 4 | 67 | Holding | RW | 401036 | 1035 | I16SO | 100 | 0
IoAnaIn_2_prefilter |  | Unfiltered value from sensor | R | 4 | 73 | Input | R | 301028 301029 | 1027 1028 | REGx2I32SO | 100 | 0
IoAnaIn_2_raw |  | Raw value from sensor | R | 4 | 76 | Input | R | 301030 301031 | 1029 1030 | REGx2I32SO | 100 | 0
IoAnaIn_2_override | 0 | Override value | R | 4 | 79 | Holding | RW | 401039 401040 | 1038 1039 | REGx2I32SO | 100 | 0 | analog_value | 1102 |  | X
IoAnaIn_2_override_en | 0 | Set to 1 to enable override | L | 4 | 82 | Coil | RW | 001026 | 1025 | LOGIC |  |  | binary_value | 1002 |  | X
IoAnaIn_2_error |  | Flag indicating any fault for signal | L | 4 | 83 | Discrete | R | 101026 | 1025 | LOGIC
IoAnaIn_2_errorFlags | 0 | Detailed fault description | H | 4 | 84 | Holding | RW | 401041 401042 | 1040 1041 | REGx2I32
IoAnaIn_2_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 87 | Holding | RW | 401043 | 1042 | I16
IoAnaIn_2_limit | 0 | Use Max and Min values as limits, or set error if outside | L | 4 | 89 | Coil | RW | 001027 | 1026 | LOGIC
IoAnaIn_2_hyst | 0 | Hysteresis limit | R | 4 | 90 | Holding | RW | 401044 | 1043 | I16SO | 100 | 0
IoAnaIn_2_accumulate | 100 | Time in milliseconds to accumulate samples before processing | I | 4 | 93 | Holding | RW | 401045 | 1044 | I16
IoAnaIn_2_valueDigits | 2 | Number of shown digits | I | 4 | 96 | Holding | RW | 401046 | 1045 | I16
IoAnaIn_3_value |  | Filtered value from sensor | R | 4 | 100 | Input | R | 301051 301052 | 1050 1051 | REGx2I32SO | 100 | 0 | analog_value | 1003
IoAnaIn_3_mode | 9 | Mode for input | X | 4 | 103 | Holding | RW | 401051 | 1050 | U8
IoAnaIn_3_unit | 0 | Unit converter | X | 4 | 104 | Holding | RW | 401052 | 1051 | U8
IoAnaIn_3_min_in | -100 | Scale for input | R | 4 | 105 | Holding | RW | 401053 401054 | 1052 1053 | REGx2I32SO | 100 | 0
IoAnaIn_3_min_out | -100 | Scale for input | R | 4 | 108 | Holding | RW | 401055 401056 | 1054 1055 | REGx2I32SO | 100 | 0
IoAnaIn_3_max_in | 10000 | Scale for input | R | 4 | 111 | Holding | RW | 401057 401058 | 1056 1057 | REGx2I32SO | 100 | 0
IoAnaIn_3_max_out | 10000 | Scale for input | R | 4 | 114 | Holding | RW | 401059 401060 | 1058 1059 | REGx2I32SO | 100 | 0
IoAnaIn_3_offset | 0 | Offset for input | R | 4 | 117 | Holding | RW | 401061 | 1060 | I16SO | 100 | 0
IoAnaIn_3_prefilter |  | Unfiltered value from sensor | R | 4 | 123 | Input | R | 301053 301054 | 1052 1053 | REGx2I32SO | 100 | 0
IoAnaIn_3_raw |  | Raw value from sensor | R | 4 | 126 | Input | R | 301055 301056 | 1054 1055 | REGx2I32SO | 100 | 0
IoAnaIn_3_override | 0 | Override value | R | 4 | 129 | Holding | RW | 401064 401065 | 1063 1064 | REGx2I32SO | 100 | 0 | analog_value | 1103 |  | X
IoAnaIn_3_override_en | 0 | Set to 1 to enable override | L | 4 | 132 | Coil | RW | 001051 | 1050 | LOGIC |  |  | binary_value | 1003 |  | X
IoAnaIn_3_error |  | Flag indicating any fault for signal | L | 4 | 133 | Discrete | R | 101051 | 1050 | LOGIC
IoAnaIn_3_errorFlags | 0 | Detailed fault description | H | 4 | 134 | Holding | RW | 401066 401067 | 1065 1066 | REGx2I32
IoAnaIn_3_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 137 | Holding | RW | 401068 | 1067 | I16
IoAnaIn_3_limit | 0 | Use Max and Min values as limits, or set error if outside | L | 4 | 139 | Coil | RW | 001052 | 1051 | LOGIC
IoAnaIn_3_hyst | 0 | Hysteresis limit | R | 4 | 140 | Holding | RW | 401069 | 1068 | I16SO | 100 | 0
IoAnaIn_3_accumulate | 100 | Time in milliseconds to accumulate samples before processing | I | 4 | 143 | Holding | RW | 401070 | 1069 | I16
IoAnaIn_4_value |  | Filtered value from sensor | R | 4 | 150 | Input | R | 301076 301077 | 1075 1076 | REGx2I32SO | 100 | 0 | analog_value | 1004
IoAnaIn_4_mode | 135 | Mode for input | X | 4 | 153 | Holding | RW | 401076 | 1075 | U8
IoAnaIn_4_unit | 0 | Unit converter | X | 4 | 154 | Holding | RW | 401077 | 1076 | U8
IoAnaIn_4_min_in | -100 | Scale for input | R | 4 | 155 | Holding | RW | 401078 401079 | 1077 1078 | REGx2I32SO | 100 | 0
IoAnaIn_4_min_out | -100 | Scale for input | R | 4 | 158 | Holding | RW | 401080 401081 | 1079 1080 | REGx2I32SO | 100 | 0
IoAnaIn_4_max_in | 10000 | Scale for input | R | 4 | 161 | Holding | RW | 401082 401083 | 1081 1082 | REGx2I32SO | 100 | 0
IoAnaIn_4_max_out | 10000 | Scale for input | R | 4 | 164 | Holding | RW | 401084 401085 | 1083 1084 | REGx2I32SO | 100 | 0
IoAnaIn_4_offset | 0 | Offset for input | R | 4 | 167 | Holding | RW | 401086 | 1085 | I16SO | 100 | 0
IoAnaIn_4_prefilter |  | Unfiltered value from sensor | R | 4 | 173 | Input | R | 301078 301079 | 1077 1078 | REGx2I32SO | 100 | 0
IoAnaIn_4_raw |  | Raw value from sensor | R | 4 | 176 | Input | R | 301080 301081 | 1079 1080 | REGx2I32SO | 100 | 0
IoAnaIn_4_override | 0 | Override value | R | 4 | 179 | Holding | RW | 401089 401090 | 1088 1089 | REGx2I32SO | 100 | 0 | analog_value | 1104 |  | X
IoAnaIn_4_override_en | 0 | Set to 1 to enable override | L | 4 | 182 | Coil | RW | 001076 | 1075 | LOGIC |  |  | binary_value | 1004 |  | X
IoAnaIn_4_error |  | Flag indicating any fault for signal | L | 4 | 183 | Discrete | R | 101076 | 1075 | LOGIC
IoAnaIn_4_errorFlags | 0 | Detailed fault description | H | 4 | 184 | Holding | RW | 401091 401092 | 1090 1091 | REGx2I32
IoAnaIn_4_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 187 | Holding | RW | 401093 | 1092 | I16
IoAnaIn_4_hyst | 0 | Hysteresis limit | R | 4 | 190 | Holding | RW | 401094 | 1093 | I16SO | 100 | 0
IoAnaIn_4_accumulate | 100 | Time in milliseconds to accumulate samples before processing | I | 4 | 193 | Holding | RW | 401095 | 1094 | I16
IoAnaIn_5_value |  | Filtered value from sensor | R | 4 | 200 | Input | R | 301101 301102 | 1100 1101 | REGx2I32SO | 100 | 0 | analog_value | 1005
IoAnaIn_5_mode | 128 | Room Temperature sensor mode | X | 4 | 203 | Holding | RW | 401101 | 1100 | U8
IoAnaIn_5_unit | 0 | Unit converter | X | 4 | 204 | Holding | RW | 401102 | 1101 | U8
IoAnaIn_5_min_in | -10 | Room Temperature Min Input | R | 4 | 205 | Holding | RW | 401103 401104 | 1102 1103 | REGx2I32SO | 100 | 0
IoAnaIn_5_min_out | -10 | Room Temperature Min Output | R | 4 | 208 | Holding | RW | 401105 401106 | 1104 1105 | REGx2I32SO | 100 | 0
IoAnaIn_5_max_in | 60 | Room Temperature Max Input | R | 4 | 211 | Holding | RW | 401107 401108 | 1106 1107 | REGx2I32SO | 100 | 0
IoAnaIn_5_max_out | 60 | Room Temperature Max Output | R | 4 | 214 | Holding | RW | 401109 401110 | 1108 1109 | REGx2I32SO | 100 | 0
IoAnaIn_5_offset | 0 | Offset for input | R | 4 | 217 | Holding | RW | 401111 | 1110 | I16SO | 100 | 0
IoAnaIn_5_prefilter |  | Unfiltered value from sensor | R | 4 | 223 | Input | R | 301103 301104 | 1102 1103 | REGx2I32SO | 100 | 0
IoAnaIn_5_raw |  | Raw value from sensor | R | 4 | 226 | Input | R | 301105 301106 | 1104 1105 | REGx2I32SO | 100 | 0
IoAnaIn_5_override | 0 | Override value | R | 4 | 229 | Holding | RW | 401114 401115 | 1113 1114 | REGx2I32SO | 100 | 0 | analog_value | 1105 |  | X
IoAnaIn_5_override_en | 0 | Set to 1 to enable override | L | 4 | 232 | Coil | RW | 001101 | 1100 | LOGIC |  |  | binary_value | 1005 |  | X
IoAnaIn_5_error |  | Flag indicating any fault for signal | L | 4 | 233 | Discrete | R | 101101 | 1100 | LOGIC
IoAnaIn_5_errorFlags | 0 | Detailed fault description | H | 4 | 234 | Holding | RW | 401116 401117 | 1115 1116 | REGx2I32
IoAnaIn_5_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 237 | Holding | RW | 401118 | 1117 | I16
IoAnaIn_5_limit | 1 | Room Temperature Limit at min/max | L | 4 | 239 | Coil | RW | 001102 | 1101 | LOGIC
IoAnaIn_5_hyst | 0 | Hysteresis limit | R | 4 | 240 | Holding | RW | 401119 | 1118 | I16SO | 100 | 0
IoAnaIn_6_value |  | Filtered value from sensor | R | 4 | 250 | Input | R | 301126 301127 | 1125 1126 | REGx2I32SO | 100 | 0 | analog_value | 1006
IoAnaIn_6_mode | 128 | Room Humidity sensor mode | X | 4 | 253 | Holding | RW | 401126 | 1125 | U8
IoAnaIn_6_unit | 0 | Unit converter | X | 4 | 254 | Holding | RW | 401127 | 1126 | U8
IoAnaIn_6_min_in | 0 | Room Humidity Min Input | R | 4 | 255 | Holding | RW | 401128 401129 | 1127 1128 | REGx2I32SO | 100 | 0
IoAnaIn_6_min_out | 0 | Room Humidity Min Output | R | 4 | 258 | Holding | RW | 401130 401131 | 1129 1130 | REGx2I32SO | 100 | 0
IoAnaIn_6_max_in | 100 | Room Humidity Max Input | R | 4 | 261 | Holding | RW | 401132 401133 | 1131 1132 | REGx2I32SO | 100 | 0
IoAnaIn_6_max_out | 100 | Room Humidity Max Output | R | 4 | 264 | Holding | RW | 401134 401135 | 1133 1134 | REGx2I32SO | 100 | 0
IoAnaIn_6_offset | 0 | Offset for input | R | 4 | 267 | Holding | RW | 401136 | 1135 | I16SO | 100 | 0
IoAnaIn_6_prefilter |  | Unfiltered value from sensor | R | 4 | 273 | Input | R | 301128 301129 | 1127 1128 | REGx2I32SO | 100 | 0
IoAnaIn_6_raw |  | Raw value from sensor | R | 4 | 276 | Input | R | 301130 301131 | 1129 1130 | REGx2I32SO | 100 | 0
IoAnaIn_6_override | 0 | Override value | R | 4 | 279 | Holding | RW | 401139 401140 | 1138 1139 | REGx2I32SO | 100 | 0 | analog_value | 1106 |  | X
IoAnaIn_6_override_en | 0 | Set to 1 to enable override | L | 4 | 282 | Coil | RW | 001126 | 1125 | LOGIC |  |  | binary_value | 1006 |  | X
IoAnaIn_6_error |  | Flag indicating any fault for signal | L | 4 | 283 | Discrete | R | 101126 | 1125 | LOGIC
IoAnaIn_6_errorFlags | 0 | Detailed fault description | H | 4 | 284 | Holding | RW | 401141 401142 | 1140 1141 | REGx2I32
IoAnaIn_6_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 287 | Holding | RW | 401143 | 1142 | I16
IoAnaIn_6_limit | 1 | Room Humidity Limit at min/max | L | 4 | 289 | Coil | RW | 001127 | 1126 | LOGIC
IoAnaIn_6_hyst | 0 | Hysteresis limit | R | 4 | 290 | Holding | RW | 401144 | 1143 | I16SO | 100 | 0
IoAnaIn_7_value |  | Filtered value from sensor | R | 4 | 300 | Input | R | 301151 301152 | 1150 1151 | REGx2I32SO | 100 | 0 | analog_value | 1007
IoAnaIn_7_mode | 128 | Room VOC sensor mode | X | 4 | 303 | Holding | RW | 401151 | 1150 | U8
IoAnaIn_7_unit | 0 | Unit converter | X | 4 | 304 | Holding | RW | 401152 | 1151 | U8
IoAnaIn_7_min_in | 0 | Room VOC Min Input | R | 4 | 305 | Holding | RW | 401153 401154 | 1152 1153 | REGx2I32SO | 100 | 0
IoAnaIn_7_min_out | 0 | Room VOC Min Output | R | 4 | 308 | Holding | RW | 401155 401156 | 1154 1155 | REGx2I32SO | 100 | 0
IoAnaIn_7_max_in | 500 | Room VOC Max Input | R | 4 | 311 | Holding | RW | 401157 401158 | 1156 1157 | REGx2I32SO | 100 | 0
IoAnaIn_7_max_out | 500 | Room VOC Max Output | R | 4 | 314 | Holding | RW | 401159 401160 | 1158 1159 | REGx2I32SO | 100 | 0
IoAnaIn_7_offset | 0 | Offset for input | R | 4 | 317 | Holding | RW | 401161 | 1160 | I16SO | 100 | 0
IoAnaIn_7_prefilter |  | Unfiltered value from sensor | R | 4 | 323 | Input | R | 301153 301154 | 1152 1153 | REGx2I32SO | 100 | 0
IoAnaIn_7_raw |  | Raw value from sensor | R | 4 | 326 | Input | R | 301155 301156 | 1154 1155 | REGx2I32SO | 100 | 0
IoAnaIn_7_override | 0 | Override value | R | 4 | 329 | Holding | RW | 401164 401165 | 1163 1164 | REGx2I32SO | 100 | 0 | analog_value | 1107 |  | X
IoAnaIn_7_override_en | 0 | Set to 1 to enable override | L | 4 | 332 | Coil | RW | 001151 | 1150 | LOGIC |  |  | binary_value | 1007 |  | X
IoAnaIn_7_error |  | Flag indicating any fault for signal | L | 4 | 333 | Discrete | R | 101151 | 1150 | LOGIC
IoAnaIn_7_errorFlags | 0 | Detailed fault description | H | 4 | 334 | Holding | RW | 401166 401167 | 1165 1166 | REGx2I32
IoAnaIn_7_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 337 | Holding | RW | 401168 | 1167 | I16
IoAnaIn_7_limit | 1 | Room VOC Limit at min/max | L | 4 | 339 | Coil | RW | 001152 | 1151 | LOGIC
IoAnaIn_7_hyst | 0 | Hysteresis limit | R | 4 | 340 | Holding | RW | 401169 | 1168 | I16SO | 100 | 0
IoAnaIn_8_value |  | Filtered value from sensor | R | 4 | 350 | Input | R | 301176 301177 | 1175 1176 | REGx2I32SO | 100 | 0 | analog_value | 1008
IoAnaIn_8_mode | 128 | Room CO2 sensor mode | X | 4 | 353 | Holding | RW | 401176 | 1175 | U8
IoAnaIn_8_unit | 0 | Unit converter | X | 4 | 354 | Holding | RW | 401177 | 1176 | U8
IoAnaIn_8_min_in | 400 | Room CO2 Min Input | R | 4 | 355 | Holding | RW | 401178 401179 | 1177 1178 | REGx2I32SO | 100 | 0
IoAnaIn_8_min_out | 400 | Room CO2 Min Output | R | 4 | 358 | Holding | RW | 401180 401181 | 1179 1180 | REGx2I32SO | 100 | 0
IoAnaIn_8_max_in | 2000 | Room CO2 Max Input | R | 4 | 361 | Holding | RW | 401182 401183 | 1181 1182 | REGx2I32SO | 100 | 0
IoAnaIn_8_max_out | 2000 | Room CO2 Max Output | R | 4 | 364 | Holding | RW | 401184 401185 | 1183 1184 | REGx2I32SO | 100 | 0
IoAnaIn_8_offset | 0 | Offset for input | R | 4 | 367 | Holding | RW | 401186 | 1185 | I16SO | 100 | 0
IoAnaIn_8_prefilter |  | Unfiltered value from sensor | R | 4 | 373 | Input | R | 301178 301179 | 1177 1178 | REGx2I32SO | 100 | 0
IoAnaIn_8_raw |  | Raw value from sensor | R | 4 | 376 | Input | R | 301180 301181 | 1179 1180 | REGx2I32SO | 100 | 0
IoAnaIn_8_override | 0 | Override value | R | 4 | 379 | Holding | RW | 401189 401190 | 1188 1189 | REGx2I32SO | 100 | 0 | analog_value | 1108 |  | X
IoAnaIn_8_override_en | 0 | Set to 1 to enable override | L | 4 | 382 | Coil | RW | 001176 | 1175 | LOGIC |  |  | binary_value | 1008 |  | X
IoAnaIn_8_error |  | Flag indicating any fault for signal | L | 4 | 383 | Discrete | R | 101176 | 1175 | LOGIC
IoAnaIn_8_errorFlags | 0 | Detailed fault description | H | 4 | 384 | Holding | RW | 401191 401192 | 1190 1191 | REGx2I32
IoAnaIn_8_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 387 | Holding | RW | 401193 | 1192 | I16
IoAnaIn_8_limit | 1 | Room CO2 Limit at min/max | L | 4 | 389 | Coil | RW | 001177 | 1176 | LOGIC
IoAnaIn_8_hyst | 0 | Hysteresis limit | R | 4 | 390 | Holding | RW | 401194 | 1193 | I16SO | 100 | 0
IoAnaIn_8_valueDigits | 2 | Number of shown digits | I | 4 | 396 | Holding | RW | 401196 | 1195 | I16
IoAnaIn_9_value |  | Filtered value from sensor | R | 4 | 400 | Input | R | 301201 301202 | 1200 1201 | REGx2I32SO | 100 | 0 | analog_value | 1009
IoAnaIn_9_mode | 9 | Mode for input | X | 4 | 403 | Holding | RW | 401201 | 1200 | U8
IoAnaIn_9_unit | 0 | Unit converter | X | 4 | 404 | Holding | RW | 401202 | 1201 | U8
IoAnaIn_9_min_in | -100 | Scale for input | R | 4 | 405 | Holding | RW | 401203 401204 | 1202 1203 | REGx2I32SO | 100 | 0
IoAnaIn_9_min_out | -100 | Scale for input | R | 4 | 408 | Holding | RW | 401205 401206 | 1204 1205 | REGx2I32SO | 100 | 0
IoAnaIn_9_max_in | 10000 | Scale for input | R | 4 | 411 | Holding | RW | 401207 401208 | 1206 1207 | REGx2I32SO | 100 | 0
IoAnaIn_9_max_out | 10000 | Scale for input | R | 4 | 414 | Holding | RW | 401209 401210 | 1208 1209 | REGx2I32SO | 100 | 0
IoAnaIn_9_offset | 0 | Offset for input | R | 4 | 417 | Holding | RW | 401211 | 1210 | I16SO | 100 | 0
IoAnaIn_9_prefilter |  | Unfiltered value from sensor | R | 4 | 423 | Input | R | 301203 301204 | 1202 1203 | REGx2I32SO | 100 | 0
IoAnaIn_9_raw |  | Raw value from sensor | R | 4 | 426 | Input | R | 301205 301206 | 1204 1205 | REGx2I32SO | 100 | 0
IoAnaIn_9_override | 0 | Override value | R | 4 | 429 | Holding | RW | 401214 401215 | 1213 1214 | REGx2I32SO | 100 | 0 | analog_value | 1109 |  | X
IoAnaIn_9_override_en | 0 | Set to 1 to enable override | L | 4 | 432 | Coil | RW | 001201 | 1200 | LOGIC |  |  | binary_value | 1009 |  | X
IoAnaIn_9_error |  | Flag indicating any fault for signal | L | 4 | 433 | Discrete | R | 101201 | 1200 | LOGIC
IoAnaIn_9_errorFlags | 0 | Detailed fault description | H | 4 | 434 | Holding | RW | 401216 401217 | 1215 1216 | REGx2I32
IoAnaIn_9_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 437 | Holding | RW | 401218 | 1217 | I16
IoAnaIn_9_hyst | 0 | Hysteresis limit | R | 4 | 440 | Holding | RW | 401219 | 1218 | I16SO | 100 | 0
IoAnaIn_10_value |  | Filtered value from sensor | R | 4 | 450 | Input | R | 301226 301227 | 1225 1226 | REGx2I32SO | 100 | 0 | analog_value | 1010
IoAnaIn_10_mode | 128 | Mode for input | X | 4 | 453 | Holding | RW | 401226 | 1225 | U8
IoAnaIn_10_unit | 0 | Unit converter | X | 4 | 454 | Holding | RW | 401227 | 1226 | U8
IoAnaIn_10_min_in | -100 | Scale for input | R | 4 | 455 | Holding | RW | 401228 401229 | 1227 1228 | REGx2I32SO | 100 | 0
IoAnaIn_10_min_out | -100 | Scale for input | R | 4 | 458 | Holding | RW | 401230 401231 | 1229 1230 | REGx2I32SO | 100 | 0
IoAnaIn_10_max_in | 10000 | Scale for input | R | 4 | 461 | Holding | RW | 401232 401233 | 1231 1232 | REGx2I32SO | 100 | 0
IoAnaIn_10_max_out | 10000 | Scale for input | R | 4 | 464 | Holding | RW | 401234 401235 | 1233 1234 | REGx2I32SO | 100 | 0
IoAnaIn_10_offset | 0 | Offset for input | R | 4 | 467 | Holding | RW | 401236 | 1235 | I16SO | 100 | 0
IoAnaIn_10_prefilter |  | Unfiltered value from sensor | R | 4 | 473 | Input | R | 301228 301229 | 1227 1228 | REGx2I32SO | 100 | 0
IoAnaIn_10_raw |  | Raw value from sensor | R | 4 | 476 | Input | R | 301230 301231 | 1229 1230 | REGx2I32SO | 100 | 0
IoAnaIn_10_override | 0 | Override value | R | 4 | 479 | Holding | RW | 401239 401240 | 1238 1239 | REGx2I32SO | 100 | 0 | analog_value | 1110 |  | X
IoAnaIn_10_override_en | 0 | Set to 1 to enable override | L | 4 | 482 | Coil | RW | 001226 | 1225 | LOGIC |  |  | binary_value | 1010 |  | X
IoAnaIn_10_error |  | Flag indicating any fault for signal | L | 4 | 483 | Discrete | R | 101226 | 1225 | LOGIC
IoAnaIn_10_errorFlags | 0 | Detailed fault description | H | 4 | 484 | Holding | RW | 401241 401242 | 1240 1241 | REGx2I32
IoAnaIn_10_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 487 | Holding | RW | 401243 | 1242 | I16
IoAnaIn_10_hyst | 0 | Hysteresis limit | R | 4 | 490 | Holding | RW | 401244 | 1243 | I16SO | 100 | 0
IoAnaIn_11_value |  | Filtered value from sensor | R | 4 | 500 | Input | R | 301251 301252 | 1250 1251 | REGx2I32SO | 100 | 0 | analog_value | 1011
IoAnaIn_11_mode | 128 | Mode for input | X | 4 | 503 | Holding | RW | 401251 | 1250 | U8
IoAnaIn_11_unit | 0 | Unit converter | X | 4 | 504 | Holding | RW | 401252 | 1251 | U8
IoAnaIn_11_min_in | -100 | Scale for input | R | 4 | 505 | Holding | RW | 401253 401254 | 1252 1253 | REGx2I32SO | 100 | 0
IoAnaIn_11_min_out | -100 | Scale for input | R | 4 | 508 | Holding | RW | 401255 401256 | 1254 1255 | REGx2I32SO | 100 | 0
IoAnaIn_11_max_in | 10000 | Scale for input | R | 4 | 511 | Holding | RW | 401257 401258 | 1256 1257 | REGx2I32SO | 100 | 0
IoAnaIn_11_max_out | 10000 | Scale for input | R | 4 | 514 | Holding | RW | 401259 401260 | 1258 1259 | REGx2I32SO | 100 | 0
IoAnaIn_11_offset | 0 | Offset for input | R | 4 | 517 | Holding | RW | 401261 | 1260 | I16SO | 100 | 0
IoAnaIn_11_prefilter |  | Unfiltered value from sensor | R | 4 | 523 | Input | R | 301253 301254 | 1252 1253 | REGx2I32SO | 100 | 0
IoAnaIn_11_raw |  | Raw value from sensor | R | 4 | 526 | Input | R | 301255 301256 | 1254 1255 | REGx2I32SO | 100 | 0
IoAnaIn_11_override | 0 | Override value | R | 4 | 529 | Holding | RW | 401264 401265 | 1263 1264 | REGx2I32SO | 100 | 0 | analog_value | 1111 |  | X
IoAnaIn_11_override_en | 0 | Set to 1 to enable override | L | 4 | 532 | Coil | RW | 001251 | 1250 | LOGIC |  |  | binary_value | 1011 |  | X
IoAnaIn_11_error |  | Flag indicating any fault for signal | L | 4 | 533 | Discrete | R | 101251 | 1250 | LOGIC
IoAnaIn_11_errorFlags | 0 | Detailed fault description | H | 4 | 534 | Holding | RW | 401266 401267 | 1265 1266 | REGx2I32
IoAnaIn_11_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 537 | Holding | RW | 401268 | 1267 | I16
IoAnaIn_11_hyst | 0 | Hysteresis limit | R | 4 | 540 | Holding | RW | 401269 | 1268 | I16SO | 100 | 0
IoAnaIn_11_valueDigits | 2 | Number of shown digits | I | 4 | 546 | Holding | RW | 401271 | 1270 | I16
IoDiIn_1_value |  | Filtered value from sensor | L | 4 | 1000 | Discrete | R | 101501 | 1500 | LOGIC |  |  | binary_value | 1101
IoDiIn_1_mode | 130 | Mode for input | X | 4 | 1001 | Holding | RW | 401501 | 1500 | U8
IoDiIn_1_invert | 1 | Invert logic signal | L | 4 | 1002 | Coil | RW | 001501 | 1500 | LOGIC
IoDiIn_1_limit | 900 | Limit for analog value | R | 4 | 1003 | Holding | RW | 401502 | 1501 | I16SO | 20 | 0
IoDiIn_1_pulse1 | 0 | Pulse counter 1 | H | 4 | 1006 | Holding | RW | 401503 401504 | 1502 1503 | REGx2I32
IoDiIn_1_pulse2 | 0 | Pulse counter 2 | H | 4 | 1009 | Holding | RW | 401505 401506 | 1504 1505 | REGx2I32
IoDiIn_1_pulserate | 0 | Pulse rate in Hz | R | 4 | 1012 | Holding | RW | 401507 | 1506 | I16SO | 100 | 0
IoDiIn_1_override | 0 | Override value | L | 4 | 1016 | Coil | RW | 001503 | 1502 | LOGIC |  |  | binary_value | 1201 |  | X
IoDiIn_1_override_en | 0 | Set to 1 to enable override | L | 4 | 1017 | Coil | RW | 001504 | 1503 | LOGIC |  |  | binary_value | 1301 |  | X
IoDiIn_1_hyst | 10 | Hysteresis limit | X | 4 | 1022 | Holding | RW | 401510 | 1509 | U8
IoDiIn_2_value |  | Filtered value from sensor | L | 4 | 1050 | Discrete | R | 101526 | 1525 | LOGIC |  |  | binary_value | 1102
IoDiIn_2_mode | 130 | Mode for input | X | 4 | 1051 | Holding | RW | 401526 | 1525 | U8
IoDiIn_2_invert | 1 | Invert logic signal | L | 4 | 1052 | Coil | RW | 001526 | 1525 | LOGIC
IoDiIn_2_limit |  | Limit for analog value | R | 4 | 1053 | Holding | RW | 401527 | 1526 | I16SO | 20 | 0
IoDiIn_2_pulse1 | 0 | Pulse counter 1 | H | 4 | 1056 | Holding | RW | 401528 401529 | 1527 1528 | REGx2I32
IoDiIn_2_pulse2 | 0 | Pulse counter 2 | H | 4 | 1059 | Holding | RW | 401530 401531 | 1529 1530 | REGx2I32
IoDiIn_2_pulserate | 0 | Pulse rate in Hz | R | 4 | 1062 | Holding | RW | 401532 | 1531 | I16SO | 100 | 0
IoDiIn_2_override | 0 | Override value | L | 4 | 1066 | Coil | RW | 001528 | 1527 | LOGIC |  |  | binary_value | 1202 |  | X
IoDiIn_2_override_en | 0 | Set to 1 to enable override | L | 4 | 1067 | Coil | RW | 001529 | 1528 | LOGIC |  |  | binary_value | 1302 |  | X
IoDiIn_2_hyst | 10 | Hysteresis limit | X | 4 | 1072 | Holding | RW | 401535 | 1534 | U8
IoDiIn_3_value |  | Filtered value from sensor | L | 4 | 1100 | Discrete | R | 101551 | 1550 | LOGIC |  |  | binary_value | 1103
IoDiIn_3_mode | 130 | Mode for input | X | 4 | 1101 | Holding | RW | 401551 | 1550 | U8
IoDiIn_3_invert | 1 | Invert logic signal | L | 4 | 1102 | Coil | RW | 001551 | 1550 | LOGIC
IoDiIn_3_limit | 180 | Limit for analog value | R | 4 | 1103 | Holding | RW | 401552 | 1551 | I16SO | 20 | 0
IoDiIn_3_pulse1 | 0 | Pulse counter 1 | H | 4 | 1106 | Holding | RW | 401553 401554 | 1552 1553 | REGx2I32
IoDiIn_3_pulse2 | 0 | Pulse counter 2 | H | 4 | 1109 | Holding | RW | 401555 401556 | 1554 1555 | REGx2I32
IoDiIn_3_pulserate | 0 | Pulse rate in Hz | R | 4 | 1112 | Holding | RW | 401557 | 1556 | I16SO | 100 | 0
IoDiIn_3_override | 0 | Override value | L | 4 | 1116 | Coil | RW | 001553 | 1552 | LOGIC |  |  | binary_value | 1203 |  | X
IoDiIn_3_override_en | 0 | Set to 1 to enable override | L | 4 | 1117 | Coil | RW | 001554 | 1553 | LOGIC |  |  | binary_value | 1303 |  | X
IoDiIn_3_hyst | 10 | Hysteresis limit | X | 4 | 1122 | Holding | RW | 401560 | 1559 | U8
IoDiIn_4_value |  | Filtered value from sensor | L | 4 | 1150 | Discrete | R | 101576 | 1575 | LOGIC |  |  | binary_value | 1104
IoDiIn_4_mode | 130 | Mode for input | X | 4 | 1151 | Holding | RW | 401576 | 1575 | U8
IoDiIn_4_invert | 0 | Invert logic signal | L | 4 | 1152 | Coil | RW | 001576 | 1575 | LOGIC
IoDiIn_4_pulse1 | 0 | Pulse counter 1 | H | 4 | 1156 | Holding | RW | 401578 401579 | 1577 1578 | REGx2I32
IoDiIn_4_pulse2 | 0 | Pulse counter 2 | H | 4 | 1159 | Holding | RW | 401580 401581 | 1579 1580 | REGx2I32
IoDiIn_4_pulserate | 0 | Pulse rate in Hz | R | 4 | 1162 | Holding | RW | 401582 | 1581 | I16SO | 100 | 0
IoDiIn_4_override | 0 | Override value | L | 4 | 1166 | Coil | RW | 001578 | 1577 | LOGIC |  |  | binary_value | 1204 |  | X
IoDiIn_4_override_en | 0 | Set to 1 to enable override | L | 4 | 1167 | Coil | RW | 001579 | 1578 | LOGIC |  |  | binary_value | 1304 |  | X
IoAnaOut_1_value | 0 | Value in % set for output | R | 5 | 0 | Holding | RW | 402501 | 2500 | I16SO | 100 | 0 | analog_value | 1201 | percent | X
IoAnaOut_1_mode | 1 | Mode for output | X | 5 | 3 | Holding | RW | 402502 | 2501 | U8
IoAnaOut_1_unit | 0 | Unit converter | X | 5 | 4 | Holding | RW | 402503 | 2502 | U8
IoAnaOut_1_min_in | 0 | Scale for output | R | 5 | 5 | Holding | RW | 402504 | 2503 | I16SO | 100 | 0
IoAnaOut_1_min_out | 0 | Scale for output | R | 5 | 8 | Holding | RW | 402505 | 2504 | I16SO | 100 | 0
IoAnaOut_1_max_in | 100 | Scale for output | R | 5 | 11 | Holding | RW | 402506 | 2505 | I16SO | 100 | 0
IoAnaOut_1_max_out | 100 | Scale for output | R | 5 | 14 | Holding | RW | 402507 | 2506 | I16SO | 100 | 0
IoAnaOut_1_offset | 0 | Offset for output | R | 5 | 17 | Holding | RW | 402508 | 2507 | I16SO | 100 | 0
IoAnaOut_1_default | 0 | Default value if communication is lost | R | 5 | 20 | Holding | RW | 402509 | 2508 | I16SO | 100 | 0 | analog_value | 1301 | percent | X
IoAnaOut_1_converted |  | Actual value on the output pin in Volt or milliampere. | R | 5 | 23 | Input | R | 302501 | 2500 | I16SO | 100 | 0 | analog_value | 1401 | volts
IoAnaOut_1_raw |  | Raw value sent to HW | R | 5 | 26 | Input | R | 302502 | 2501 | I16SO | 100 | 0
IoAnaOut_1_override | 0 | Override value | R | 5 | 29 | Holding | RW | 402510 | 2509 | I16SO | 100 | 0 | analog_value | 1501 | percent | X
IoAnaOut_1_override_en | 0 | Set to 1 to enable override | L | 5 | 32 | Coil | RW | 002501 | 2500 | LOGIC |  |  | binary_value | 1401 |  | X
IoAnaOut_1_ramp | 0 | Limits the change in output to this value in units (%?) / s. A value of 0 means that the output will not be limited. | R | 5 | 33 | Holding | RW | 402511 | 2510 | I16SO | 100 | 0
IoAnaOut_1_pulse_period | 60 | Period time for pulse output | I | 5 | 36 | Holding | RW | 402512 | 2511 | I16
IoAnaOut_2_value | 0 | Value in % set for output | R | 5 | 50 | Holding | RW | 402526 | 2525 | I16SO | 100 | 0 | analog_value | 1202 | percent | X
IoAnaOut_2_mode | 1 | Mode for output | X | 5 | 53 | Holding | RW | 402527 | 2526 | U8
IoAnaOut_2_unit | 0 | Unit converter | X | 5 | 54 | Holding | RW | 402528 | 2527 | U8
IoAnaOut_2_min_in | 0 | Scale for output | R | 5 | 55 | Holding | RW | 402529 | 2528 | I16SO | 100 | 0
IoAnaOut_2_min_out | 0 | Scale for output | R | 5 | 58 | Holding | RW | 402530 | 2529 | I16SO | 100 | 0
IoAnaOut_2_max_in | 100 | Scale for output | R | 5 | 61 | Holding | RW | 402531 | 2530 | I16SO | 100 | 0
IoAnaOut_2_max_out | 100 | Scale for output | R | 5 | 64 | Holding | RW | 402532 | 2531 | I16SO | 100 | 0
IoAnaOut_2_offset | 0 | Offset for output | R | 5 | 67 | Holding | RW | 402533 | 2532 | I16SO | 100 | 0
IoAnaOut_2_default | 0 | Default value if communication is lost | R | 5 | 70 | Holding | RW | 402534 | 2533 | I16SO | 100 | 0 | analog_value | 1302 | percent | X
IoAnaOut_2_converted |  | Actual value on the output pin in Volt or milliampere. | R | 5 | 73 | Input | R | 302526 | 2525 | I16SO | 100 | 0 | analog_value | 1402 | volts
IoAnaOut_2_raw |  | Raw value sent to HW | R | 5 | 76 | Input | R | 302527 | 2526 | I16SO | 100 | 0
IoAnaOut_2_override | 0 | Override value | R | 5 | 79 | Holding | RW | 402535 | 2534 | I16SO | 100 | 0 | analog_value | 1502 | percent | X
IoAnaOut_2_override_en | 0 | Set to 1 to enable override | L | 5 | 82 | Coil | RW | 002526 | 2525 | LOGIC |  |  | binary_value | 1402 |  | X
IoAnaOut_2_ramp | 0 | Limits the change in output to this value in units (%?) / s. A value of 0 means that the output will not be limited. | R | 5 | 83 | Holding | RW | 402536 | 2535 | I16SO | 100 | 0
IoAnaOut_2_pulse_period | 60 | Period time for pulse output | I | 5 | 86 | Holding | RW | 402537 | 2536 | I16
IoAnaOut_3_value | 0 | Value in % set for output | R | 5 | 100 | Holding | RW | 402551 | 2550 | I16SO | 100 | 0 | analog_value | 1203 | percent | X
IoAnaOut_3_mode | 1 | Mode for output | X | 5 | 103 | Holding | RW | 402552 | 2551 | U8
IoAnaOut_3_unit | 0 | Unit converter | X | 5 | 104 | Holding | RW | 402553 | 2552 | U8
IoAnaOut_3_min_in | 0 | Scale for output | R | 5 | 105 | Holding | RW | 402554 | 2553 | I16SO | 100 | 0
IoAnaOut_3_min_out | 0 | Scale for output | R | 5 | 108 | Holding | RW | 402555 | 2554 | I16SO | 100 | 0
IoAnaOut_3_max_in | 100 | Scale for output | R | 5 | 111 | Holding | RW | 402556 | 2555 | I16SO | 100 | 0
IoAnaOut_3_max_out | 100 | Scale for output | R | 5 | 114 | Holding | RW | 402557 | 2556 | I16SO | 100 | 0
IoAnaOut_3_offset | 0 | Offset for output | R | 5 | 117 | Holding | RW | 402558 | 2557 | I16SO | 100 | 0
IoAnaOut_3_default | 0 | Default value if communication is lost | R | 5 | 120 | Holding | RW | 402559 | 2558 | I16SO | 100 | 0 | analog_value | 1303 | percent | X
IoAnaOut_3_converted |  | Actual value on the output pin in Volt or milliampere. | R | 5 | 123 | Input | R | 302551 | 2550 | I16SO | 100 | 0 | analog_value | 1403 | volts
IoAnaOut_3_raw |  | Raw value sent to HW | R | 5 | 126 | Input | R | 302552 | 2551 | I16SO | 100 | 0
IoAnaOut_3_override | 0 | Override value | R | 5 | 129 | Holding | RW | 402560 | 2559 | I16SO | 100 | 0 | analog_value | 1503 | percent | X
IoAnaOut_3_override_en | 0 | Set to 1 to enable override | L | 5 | 132 | Coil | RW | 002551 | 2550 | LOGIC |  |  | binary_value | 1403 |  | X
IoAnaOut_3_ramp | 0 | Limits the change in output to this value in units (%?) / s. A value of 0 means that the output will not be limited. | R | 5 | 133 | Holding | RW | 402561 | 2560 | I16SO | 100 | 0
IoAnaOut_3_pulse_period | 60 | Period time for pulse output | I | 5 | 136 | Holding | RW | 402562 | 2561 | I16
IoAnaOut_4_value | 0 | Value in % set for output | R | 5 | 150 | Holding | RW | 402576 | 2575 | I16SO | 100 | 0 | analog_value | 1204 | percent | X
IoAnaOut_4_mode | 1 | Mode for output | X | 5 | 153 | Holding | RW | 402577 | 2576 | U8
IoAnaOut_4_unit | 0 | Unit converter | X | 5 | 154 | Holding | RW | 402578 | 2577 | U8
IoAnaOut_4_min_in | 0 | Scale for output | R | 5 | 155 | Holding | RW | 402579 | 2578 | I16SO | 100 | 0
IoAnaOut_4_min_out | 0 | Scale for output | R | 5 | 158 | Holding | RW | 402580 | 2579 | I16SO | 100 | 0
IoAnaOut_4_max_in | 100 | Scale for output | R | 5 | 161 | Holding | RW | 402581 | 2580 | I16SO | 100 | 0
IoAnaOut_4_max_out | 100 | Scale for output | R | 5 | 164 | Holding | RW | 402582 | 2581 | I16SO | 100 | 0
IoAnaOut_4_offset | 0 | Offset for output | R | 5 | 167 | Holding | RW | 402583 | 2582 | I16SO | 100 | 0
IoAnaOut_4_default | 0 | Default value if communication is lost | R | 5 | 170 | Holding | RW | 402584 | 2583 | I16SO | 100 | 0 | analog_value | 1304 | percent | X
IoAnaOut_4_converted |  | Actual value on the output pin in Volt or milliampere. | R | 5 | 173 | Input | R | 302576 | 2575 | I16SO | 100 | 0 | analog_value | 1404 | volts
IoAnaOut_4_raw |  | Raw value sent to HW | R | 5 | 176 | Input | R | 302577 | 2576 | I16SO | 100 | 0
IoAnaOut_4_override | 0 | Override value | R | 5 | 179 | Holding | RW | 402585 | 2584 | I16SO | 100 | 0 | analog_value | 1504 | percent | X
IoAnaOut_4_override_en | 0 | Set to 1 to enable override | L | 5 | 182 | Coil | RW | 002576 | 2575 | LOGIC |  |  | binary_value | 1404 |  | X
IoAnaOut_4_ramp | 0 | Limits the change in output to this value in units (%?) / s. A value of 0 means that the output will not be limited. | R | 5 | 183 | Holding | RW | 402586 | 2585 | I16SO | 100 | 0
IoAnaOut_4_pulse_period | 60 | Period time for pulse output | I | 5 | 186 | Holding | RW | 402587 | 2586 | I16
IoDo_1_value | 0 | Value set for output | L | 5 | 1000 | Coil | RW | 003001 | 3000 | LOGIC |  |  | binary_value | 1501 |  | X
IoDo_1_mode | 3 | Mode for output | X | 5 | 1001 | Holding | RW | 403001 | 3000 | U8
IoDo_1_default | 0 | Default value if communication is lost | L | 5 | 1002 | Coil | RW | 003002 | 3001 | LOGIC |  |  | binary_value | 1601 |  | X
IoDo_1_override | 0 | Override value | L | 5 | 1003 | Coil | RW | 003003 | 3002 | LOGIC |  |  | binary_value | 1701 |  | X
IoDo_1_override_en | 0 | Set to 1 to enable override | L | 5 | 1004 | Coil | RW | 003004 | 3003 | LOGIC |  |  | binary_value | 1801 |  | X
IoDo_1_out |  | Current value of output | L | 5 | 1005 | Discrete | R | 103001 | 3000 | LOGIC |  |  | binary_value | 1901
IoDo_1_invert | 0 | Set to 1 to invert output | L | 5 | 1006 | Coil | RW | 003005 | 3004 | LOGIC
IoDo_2_value | 0 | Value set for output | L | 5 | 1050 | Coil | RW | 003026 | 3025 | LOGIC |  |  | binary_value | 1502 |  | X
IoDo_2_mode | 3 | Mode for output | X | 5 | 1051 | Holding | RW | 403026 | 3025 | U8
IoDo_2_default | 0 | Default value if communication is lost | L | 5 | 1052 | Coil | RW | 003027 | 3026 | LOGIC |  |  | binary_value | 1602 |  | X
IoDo_2_override | 0 | Override value | L | 5 | 1053 | Coil | RW | 003028 | 3027 | LOGIC |  |  | binary_value | 1702 |  | X
IoDo_2_override_en | 0 | Set to 1 to enable override | L | 5 | 1054 | Coil | RW | 003029 | 3028 | LOGIC |  |  | binary_value | 1802 |  | X
IoDo_2_out |  | Current value of output | L | 5 | 1055 | Discrete | R | 103026 | 3025 | LOGIC |  |  | binary_value | 1902
IoDo_2_invert | 0 | Set to 1 to invert output | L | 5 | 1056 | Coil | RW | 003030 | 3029 | LOGIC
IoDo_3_value | 0 | Value set for output | L | 5 | 1100 | Coil | RW | 003051 | 3050 | LOGIC |  |  | binary_value | 1503 |  | X
IoDo_3_mode | 3 | Mode for output | X | 5 | 1101 | Holding | RW | 403051 | 3050 | U8
IoDo_3_default | 0 | Default value if communication is lost | L | 5 | 1102 | Coil | RW | 003052 | 3051 | LOGIC |  |  | binary_value | 1603 |  | X
IoDo_3_override | 0 | Override value | L | 5 | 1103 | Coil | RW | 003053 | 3052 | LOGIC |  |  | binary_value | 1703 |  | X
IoDo_3_override_en | 0 | Set to 1 to enable override | L | 5 | 1104 | Coil | RW | 003054 | 3053 | LOGIC |  |  | binary_value | 1803 |  | X
IoDo_3_out |  | Current value of output | L | 5 | 1105 | Discrete | R | 103051 | 3050 | LOGIC |  |  | binary_value | 1903
IoDo_3_invert | 0 | Set to 1 to invert output | L | 5 | 1106 | Coil | RW | 003055 | 3054 | LOGIC
Disp_BrightnessFull | 100 | Display brightness, full (%) | X | 6 | 0 | Holding | RW | 406001 | 6000 | U8 |  |  | analog_value | 8001 | percent | X
Disp_BrightnessDim | 20 | Display brightness, dimmed (%) | X | 6 | 1 | Holding | RW | 406002 | 6001 | U8 |  |  | analog_value | 8011 | percent | X
Disp_TimeFull | 30 | Display time in full mode. 0 = Never dim. | I | 6 | 2 | Holding | RW | 406003 | 6002 | I16 |  |  | analog_value | 8021 | seconds | X
Disp_TimeDim | 30 | Display time in dimmed mode. 0 = Never off. | I | 6 | 4 | Holding | RW | 406004 | 6003 | I16 |  |  | analog_value | 8031 | seconds | X
DisplayStartupMode | 4 | What to display during device startup | X | 6 | 8 | Holding | RW | 406005 | 6004 | U8
rt_text_font | 0 | What font to use for the display text | X | 8 | 275 | Holding | RW | 408145 | 8144 | U8
rt_text_mode | 0 | Single or dual row text in display | X | 8 | 276 | Holding | RW | 408146 | 8145 | U8
rt_text_display_scroll_mode | 0 | Scroll mode | X | 8 | 277 | Holding | RW | 408147 | 8146 | U8
rt_text_display_scroll_speed | 100 | Time in ms between scrolling one pixel | I | 8 | 278 | Holding | RW | 408148 | 8147 | I16
rt_text_visability | 0 | When to show the custom text | X | 8 | 280 | Holding | RW | 408149 | 8148 | U8
rt_text_timeleft | 0 | Time to show the custom text | I | 8 | 281 | Holding | RW | 408150 | 8149 | I16
rt_text_row_1 |  | String to show on row 1 in the display | $ | 8 | 283 | Holding | RW | 408151 - 408182 | 8150 - 8181 | STRING
rt_text_row_2 |  | String to show on row 2 in the display | $ | 8 | 286 | Holding | RW | 408183 - 408214 | 8182 - 8213 | STRING
App_EnableMenuFan | 1 | Enable Fan menu page | X | 10 | 0 | Holding | RW | 407001 | 7000 | U8
App_EnableMenuForcedVent | 1 | Enable Forced ventilation menu page | X | 10 | 1 | Holding | RW | 407002 | 7001 | U8
App_EnableMenuHumidity | 1 | Enable Humidity menu page | X | 10 | 2 | Holding | RW | 407003 | 7002 | U8
App_EnableMenuCO2 | 1 | Enable CO2 menu page | X | 10 | 3 | Holding | RW | 407004 | 7003 | U8
App_EnableMenuVOC | 1 | Enable VOC menu page | X | 10 | 4 | Holding | RW | 407005 | 7004 | U8
App_EnableSetpoint | 1 | Enable setpoint setting from display | X | 10 | 5 | Holding | RW | 407006 | 7005 | U8
App_EnableMenuMode | 0 | Enable Mode menu page | X | 10 | 7 | Holding | RW | 407008 | 7007 | U8
App_ModeMenuTitle | MODE | Mode menu title | $ | 10 | 8
App_ModeMenuAutoText | AUTO | Mode menu Auto state text | $ | 10 | 11
App_ModeMenuOffText | OFF | Mode menu Off state text | $ | 10 | 14
App_ModeMenuUnoccText | OFF | Mode menu Unoccupied state text | $ | 10 | 17
App_ModeMenuStandbyText | ECO | Mode menu Standby state text | $ | 10 | 20
App_ModeMenuOccText | ON | Mode menu Occupied state text | $ | 10 | 23
App_ModeMenuBypassText | MAX | Mode menu Bypass state text | $ | 10 | 26
App_ModeMenuOffEnable | 1 | Mode menu Off state enable | L | 10 | 29
App_ModeMenuUnoccEnable | 0 | Mode menu Unoccupied state enable | L | 10 | 30
App_ModeMenuStandbyEnable | 0 | Mode menu Standby state enable | L | 10 | 31
App_ModeMenuOccEnable | 1 | Mode menu Occupied state enable | L | 10 | 32
App_ModeMenuBypassEnable | 0 | Mode menu Bypass state enable | L | 10 | 33
App_ChangeOverMenuTitle | CHOVER | Change-over menu title | $ | 10 | 34
App_ChangeOverMenuAutoText | AUTO | Change-over menu Auto state text | $ | 10 | 37
App_ChangeOverMenuHeatText | HEAT | Change-over menu Heat state text | $ | 10 | 40
App_ChangeOverMenuCoolText | COOL | Change-over menu Cool state text | $ | 10 | 43
App_ChangeOverMenuAutoEnable | 1 | Change-over menu Auto state enable | L | 10 | 46
App_ChangeOverMenuHeatEnable | 1 | Change-over menu Heat state enable | L | 10 | 47
App_ChangeOverMenuCoolEnable | 1 | Change-over menu Cool state enable | L | 10 | 48
App_EnableMenuChangeOver | 0 | Enable Change-over menu page | X | 10 | 49 | Holding | RW | 407009 | 7008 | U8
SCD40_ASC_enable | 1 | Enable automatic calibration of CO2 sensor | L | 10 | 50 | Coil | RW | 000101 | 100 | LOGIC
SCD40_ASC_target | 400 | Automatic calibration of CO2 sensor target | I | 10 | 51 | Holding | RW | 400101 | 100 | I16
SCD40_factory_reset | 1 | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset | L | 10 | 53 | Coil | RW | 000102 | 101 | LOGIC
SCD40_FRC_result | 0 | Calculated offset after calibration or -9999 if failed. | I | 10 | 54 | Holding | RW | 400102 | 101 | I16
SCD40_FRC_enable | 0 | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done | L | 10 | 56 | Coil | RW | 000103 | 102 | LOGIC
SCD40_FRC_target | 400 | Current actual CO2 value to calibrate to | I | 10 | 57 | Holding | RW | 400103 | 102 | I16
PLA | 254 |  | X | 241 | 0
ELA | 30 |  | X | 241 | 1
Ver_Minor |  |  | X | 241 | 16 | Input | R | 300007 | 6 | U8
Ver_Major |  |  | X | 241 | 17 | Input | R | 300006 | 5 | U8
MODEL_ALIAS |  | Model number | I | 241 | 36 | Input | R | 300050 | 49 | I16
Model |  | Model number | I | 241 | 36 | Input | R | 300002 | 1 | I16
Ver_Branch |  |  | X | 241 | 40 | Input | R | 300008 | 7 | U8
Ver_Number |  |  | X | 241 | 41 | Input | R | 300009 | 8 | U8
SerialNumberString | 0 |  | $ | 241 | 60
ControllerName | RegioX |  | $ | 241 | 63 | Holding | RW | 400039 - 400070 | 38 - 69 | STRING
ControllerProject | 0 |  | $ | 241 | 66
ControllerDescription |  | Controller description | $ | 241 | 69
ControllerLocation |  | Controller location | $ | 241 | 72
UptimeMillisec | 0 |  | I | 241 | 75
UptimeSec | 0 |  | H | 241 | 77
GitCommit |  | Internal revision number | I | 241 | 80 | Input | R | 300011 | 10 | I16
ModelName | 0 |  | $ | 241 | 100
VendorName | AB Regin |  | $ | 241 | 109
OSid |  | Application OPERATING_SYSTEM_ID | H | 241 | 138
BACnetCommitSettings | 0 | Commit BACnet settings | L | 242 | 59
BACnetDeviceID | -1 | BACnet device ID | H | 242 | 60
BACnetDeviceObjectName | RegioX | BACnet device object name | $ | 242 | 63
BACnetSegmentationSupported | 3 | BACnet segmentation supported | X | 242 | 66
BACnetAPDUTimeout | 3000 | BACnet APDU timeout | I | 242 | 67
BACnetAPDUsegmentTimeout | 2000 | BACnet APDU segment timeout | I | 242 | 69
BACnetConfLn | 125 | BACnet configuration load number | X | 242 | 71
BACnetDataLn | 124 | BACnet data load number | X | 242 | 72
BACnetWideCharacterSetEncoding | 0 | BACnet wide character set encoding | X | 242 | 73
BACnetVendorName | AB Regin | BACnet vendor name | $ | 242 | 75
BACnetVendorIdentifier | 264 | BACnet vendor identifier | I | 242 | 78
BACnetMstpMAC_Port_1 | 0 | BACnet MS/TP MAC port 1 | X | 242 | 85
BACnetMstpMaxAPDUlenAccepted_Port_1 | 480 | BACnet MS/TP max accepted APDU length port 1 | I | 242 | 86
BACnetMstpNrOfAPDUretries_Port_1 | 3 | BACnet MS/TP no of APDU retries port 1 | X | 242 | 88
BACnetMstpMaxMasterAddr_Port_1 | 127 | BACnet MS/TP max master address port 1 | X | 242 | 89
BACnetMstpMaxInfoFrames_Port_1 | 1 | BACnet MS/TP max info frames port 1 | X | 242 | 90
BACnetIpEnable | 0 | BACnet IP enable | L | 242 | 112
BACnetMaxServerCOV | 100 | BACnet max server COV | I | 242 | 135
BACnetPassword | gioP5TJBP8FASqREs6zX | BACnet password | $ | 242 | 139
BACnetDatabaseRevisionTicker | 0 | BACnet database revision ticker | I | 242 | 142
ModbusUnitID | 1 | Active Modbus unit ID | X | 242 | 172 | Holding | RW | 400002 | 1 | U8
ModbusCharTimeout_Port_1 | 3 |  | I | 242 | 197 | Holding | RW | 400008 | 7 | I16
ModbusAnswerDelay_Port_1 | 5 |  | I | 242 | 199 | Holding | RW | 400009 | 8 | I16
Mode_Port_1 | 2 | Active RS485 port mode/protocol | X | 248 | 0
Format_Port_1 | 112 | Active RS485 port format | X | 248 | 35
TimeOut_Port_1 | 0 |  | X | 248 | 38
Baud_Port_1 | 0 | Active RS485 port baud rate | X | 248 | 41
Note on K3: LOGIC: Used for True/False values, only allowed for "Discrete inputs" and "Coils" U8: One 8 bit unsigned integer variable to/from LSB of one register I16: One 16 bit integer variable to/from one register I16SO: Floating point variable converted to 16 bit integer to/from one register. Scale and Offset used REGx2IEEE: First register: MSW of floating point variable to/from one 16-bit register (IEEE) Second register: LSW of floating point variable to/from one 16-bit register (IEEE) REGx2I32: First register: MSW of 32 bit integer variable to/from one 16-bit register Second register: LSW of 32 bit integer variable to/from one 16-bit register REGx2I32SO: First register: MSW of 32 bit integer converted from floating point variable. Scale & Offset used. R/O Second register: LSW of 32 bit integer converted from floating point variable. Scale & Offset used. R/O
Note on C5: 23040 = Do nothing 23041 = Cools reset 23042 = Upgrade 23043 = Colds 23044 = Power up 23045 = Warm reset 23046 = Save config as user default 23047 = Restore config from user default 23048 = Switch to Bluetooth Direct Test Mode
Note on C8: 0 = Inactive 2 = EXOline slave 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on N8: 1 = Inactive 3 = EXOline slave 14 = BACnet 16 = Modbus slave 22 = EXOline/Modbus autodetect
Note on C9: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s
Note on N9: 1 = 9600 bits/s 3 = 2400 bits/s 4 = 1200 bits/s 16 = 19200 bits/s 18 = 38400 bits/s 19 = 57600 bits/s 21 = 115200 bits/s 22 = 230400 bits/s 23 = 460800 bits/s 26 = 921k6 bits/s 27 = 1000000 bits/s 28 = 250000 bits/s
Note on C10: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on N10: 17 = 8 bit, no parity, 1 stop bit 25 = 8 bit, no parity, 2 stop bits 49 = 8 bit, even parity, 1 stop bit 57 = 8 bit, even parity, 2 stop bits 113 = 8 bit, odd parity, 1 stop bit 121 = 8 bit, odd parity, 2 stop bits
Note on C16: 0 = Disabled 1 = Set outputs to default values 2 = Set controller state to a default value 3 = Set outputs to default values, start device in offline mode
Note on N16: 1 = Disabled 2 = Set outputs to default values 3 = Set controller state to a default value 4 = Set outputs to default values, start device in offline mode
Note on C20: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on C22: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on C24: 0 = No faults 1 = Internal Error 2 = Calibration Lost during startup 4 = Calibration memory failed
Note on C33: 0 = Always off 1 = Always on 2 = On at startup 3 = On with button press
Note on C55: 0 = Heating mode 1 = Cooling mode
Note on N55: 1 = Heating mode 2 = Cooling mode
Note on C56: 0 = Heating mode 1 = Cooling mode
Note on N56: 1 = Heating mode 2 = Cooling mode
Note on C60: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on N60: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on C61: 0 = Controller mode Off 1 = Controller mode Heating 2 = Controller mode Cooling
Note on N61: 1 = Controller mode Off 2 = Controller mode Heating 3 = Controller mode Cooling
Note on C62: 0 = Heating mode 1 = Cooling mode
Note on N62: 1 = Heating mode 2 = Cooling mode
Note on C63: 0 = Heating mode 1 = Cooling mode
Note on N63: 1 = Heating mode 2 = Cooling mode
Note on C109: 0 = Off 1 = Green 2 = Yellow 3 = Red
Note on N109: 1 = Off 2 = Green 3 = Yellow 4 = Red
Note on C118: 0 = Unused 1 = Room temperature 2 = CO2 Level 3 = Air Flow 4 = Change over medium temperature 5 = Extra Zone Temperature 6 = Supply air temperature 7 = Relative humidity 8 = Damper position 9 = Extract temperature 10 = VAV Change over air temperature 11 = Room temperature 0-10V 12 = VOC index 20 = Presence DI 21 = Window contact DI 22 = Change-over DI 23 = Condensation DI 24 = VAV Change-over DI 25 = Alarm DI
Note on C119: 0 = Unused 1 = Room temperature 2 = CO2 Level 3 = Air Flow 4 = Change over medium temperature 5 = Extra Zone Temperature 6 = Supply air temperature 7 = Relative humidity 8 = Damper position 9 = Extract temperature 10 = VAV Change over air temperature 11 = Room temperature 0-10V 12 = VOC index 20 = Presence DI 21 = Window contact DI 22 = Change-over DI 23 = Condensation DI 24 = VAV Change-over DI 25 = Alarm DI
Note on C120: 0 = Unused 1 = Room temperature 2 = CO2 Level 3 = Air Flow 4 = Change over medium temperature 5 = Extra Zone Temperature 6 = Supply air temperature 7 = Relative humidity 8 = Damper position 9 = Extract temperature 10 = VAV Change over air temperature 11 = Room temperature 0-10V 12 = VOC index 20 = Presence DI 21 = Window contact DI 22 = Change-over DI 23 = Condensation DI 24 = VAV Change-over DI 25 = Alarm DI
Note on C121: 0 = Unused 1 = Room temperature 2 = CO2 Level 3 = Air Flow 4 = Change over medium temperature 5 = Extra Zone Temperature 6 = Supply air temperature 7 = Relative humidity 8 = Damper position 9 = Extract temperature 10 = VAV Change over air temperature 11 = Room temperature 0-10V 12 = VOC index 20 = Presence DI 21 = Window contact DI 22 = Change-over DI 23 = Condensation DI 24 = VAV Change-over DI 25 = Alarm DI
Note on C122: 0 = Unused 1 = Heat 1 output 0-10V 2 = Cool1 output 0-10V 3 = VAV1 output 0-10V 4 = Heat 2 output 0-10V 5 = Cool2 output 0-10V 6 = VAV2 output 0-10V 7 = Change-Over output 0-10V 8 = Heat/Cool 6-way valve output 0-10V 9 = Extra Zone output 0-10V 10 = EC Fan output 0-10V 11 = CO2 control output 0-10V 12 = Humidify output 0-10V 13 = Dehumidify output 0-10V 14 = VAV change-Over output 0-10V 15 = VOC control output 0-10V 20 = Heat 1 output thermal (PWM) 21 = Cool 1 output thermal (PWM) 22 = Heat 2 output thermal (PWM) 23 = Cool 2 output thermal (PWM) 24 = Extra Zone output thermal (PWM) 25 = Change-Over output thermal (PWM) 26 = Heat/Cool 6-way valve output thermal (PWM) 27 = Heat 1 output on/off 28 = Cool 1 output on/off 29 = Heat 2 output on/off 30 = Cool 2 output on/off 31 = Extra Zone output on/off 32 = Fan speed 1 33 = Fan speed 2 34 = Fan speed 3 35 = Forced ventilation 36 = Light control 37 = Extra Zone active 38 = Sum Alarm 50 = CI driver
Note on C123: 0 = Unused 1 = Heat 1 output 0-10V 2 = Cool1 output 0-10V 3 = VAV1 output 0-10V 4 = Heat 2 output 0-10V 5 = Cool2 output 0-10V 6 = VAV2 output 0-10V 7 = Change-Over output 0-10V 8 = Heat/Cool 6-way valve output 0-10V 9 = Extra Zone output 0-10V 10 = EC Fan output 0-10V 11 = CO2 control output 0-10V 12 = Humidify output 0-10V 13 = Dehumidify output 0-10V 14 = VAV change-Over output 0-10V 15 = VOC control output 0-10V 20 = Heat 1 output thermal (PWM) 21 = Cool 1 output thermal (PWM) 22 = Heat 2 output thermal (PWM) 23 = Cool 2 output thermal (PWM) 24 = Extra Zone output thermal (PWM) 25 = Change-Over output thermal (PWM) 26 = Heat/Cool 6-way valve output thermal (PWM) 27 = Heat 1 output on/off 28 = Cool 1 output on/off 29 = Heat 2 output on/off 30 = Cool 2 output on/off 31 = Extra Zone output on/off 32 = Fan speed 1 33 = Fan speed 2 34 = Fan speed 3 35 = Forced ventilation 36 = Light control 37 = Extra Zone active 38 = Sum Alarm 50 = CI driver
Note on C124: 0 = Unused 1 = Heat 1 output 0-10V 2 = Cool1 output 0-10V 3 = VAV1 output 0-10V 4 = Heat 2 output 0-10V 5 = Cool2 output 0-10V 6 = VAV2 output 0-10V 7 = Change-Over output 0-10V 8 = Heat/Cool 6-way valve output 0-10V 9 = Extra Zone output 0-10V 10 = EC Fan output 0-10V 11 = CO2 control output 0-10V 12 = Humidify output 0-10V 13 = Dehumidify output 0-10V 14 = VAV change-Over output 0-10V 15 = VOC control output 0-10V 20 = Heat 1 output thermal (PWM) 21 = Cool 1 output thermal (PWM) 22 = Heat 2 output thermal (PWM) 23 = Cool 2 output thermal (PWM) 24 = Extra Zone output thermal (PWM) 25 = Change-Over output thermal (PWM) 26 = Heat/Cool 6-way valve output thermal (PWM) 27 = Heat 1 output on/off 28 = Cool 1 output on/off 29 = Heat 2 output on/off 30 = Cool 2 output on/off 31 = Extra Zone output on/off 32 = Fan speed 1 33 = Fan speed 2 34 = Fan speed 3 35 = Forced ventilation 36 = Light control 37 = Extra Zone active 38 = Sum Alarm 50 = CI driver
Note on C125: 0 = Unused 1 = Heat 1 output 0-10V 2 = Cool1 output 0-10V 3 = VAV1 output 0-10V 4 = Heat 2 output 0-10V 5 = Cool2 output 0-10V 6 = VAV2 output 0-10V 7 = Change-Over output 0-10V 8 = Heat/Cool 6-way valve output 0-10V 9 = Extra Zone output 0-10V 10 = EC Fan output 0-10V 11 = CO2 control output 0-10V 12 = Humidify output 0-10V 13 = Dehumidify output 0-10V 14 = VAV change-Over output 0-10V 15 = VOC control output 0-10V 20 = Heat 1 output thermal (PWM) 21 = Cool 1 output thermal (PWM) 22 = Heat 2 output thermal (PWM) 23 = Cool 2 output thermal (PWM) 24 = Extra Zone output thermal (PWM) 25 = Change-Over output thermal (PWM) 26 = Heat/Cool 6-way valve output thermal (PWM) 27 = Heat 1 output on/off 28 = Cool 1 output on/off 29 = Heat 2 output on/off 30 = Cool 2 output on/off 31 = Extra Zone output on/off 32 = Fan speed 1 33 = Fan speed 2 34 = Fan speed 3 35 = Forced ventilation 36 = Light control 37 = Extra Zone active 38 = Sum Alarm 50 = CI driver
Note on C126: 0 = Unused 1 = Heat 1 2 = Cool1 3 = VAV1 4 = Heat 2 5 = Cool2 6 = VAV2 7 = Change-Over 8 = Heat/Cool 6-way valve 9 = Change-Over VAV
Note on C127: 0 = Unused 1 = Heat 1 2 = Cool1 3 = VAV1 4 = Heat 2 5 = Cool2 6 = VAV2 7 = Change-Over 8 = Heat/Cool 6-way valve 9 = Change-Over VAV
Note on C128: 0 = Unused 1 = Heat 1 2 = Cool1 3 = VAV1 4 = Heat 2 5 = Cool2 6 = VAV2 7 = Change-Over 8 = Heat/Cool 6-way valve 9 = Change-Over VAV
Note on C167: 0 = Manual heating 1 = Manual cooling 2 = Digital input 3 = Analog input, simple 4 = Analog input, advanced
Note on N167: 1 = Manual heating 2 = Manual cooling 3 = Digital input 4 = Analog input, simple 5 = Analog input, advanced
Note on C172: 0 = Manual heating 1 = Manual cooling 2 = Digital input 3 = Analog input, simple 4 = Analog input, advanced
Note on N172: 1 = Manual heating 2 = Manual cooling 3 = Digital input 4 = Analog input, simple 5 = Analog input, advanced
Note on C196: 0 = Unused 1 = Heat 2 = Cool
Note on C202: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on C213: 0 = Unused 1 = Active when heating 2 = Active when cooling 3 = Active when heating and cooling
Note on C220: 0 = No Control 1 = Controlled by heating 2 = Controlled by Cooling 3 = Controlled by both heating and cooling
Note on C221: 0 = Fan off 1 = Fan at low speed 2 = Fan at medium speed 3 = Fan at high speed 4 = Fan in Auto mode
Note on N221: 1 = Fan off 2 = Fan at low speed 3 = Fan at medium speed 4 = Fan at high speed 5 = Fan in Auto mode
Note on C233: 0 = No Control 1 = Controlled by heating 2 = Controlled by Cooling 3 = Controlled by both heating and cooling
Note on C244: 0 = Unused 1 = Active when cooling or heating is over limit 2 = Active when cooling is over limit
Note on C246: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on N246: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on C247: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on N247: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on C248: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on N248: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on C249: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on N249: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on C250: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on N250: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on C274: 0 = Heating mode 1 = Cooling mode
Note on N274: 1 = Heating mode 2 = Cooling mode
Note on C275: 0 = Heating mode 1 = Cooling mode
Note on N275: 1 = Heating mode 2 = Cooling mode
Note on C292: 0 = Off 1 = Manual 2 = Auto
Note on N292: 1 = Off 2 = Manual 3 = Auto
Note on C293: 0 = Off 1 = Manual 2 = Auto
Note on N293: 1 = Off 2 = Manual 3 = Auto
Note on C294: 0 = Off 1 = Manual 2 = Auto
Note on N294: 1 = Off 2 = Manual 3 = Auto
Note on C295: 0 = Off 1 = Manual 2 = Auto
Note on N295: 1 = Off 2 = Manual 3 = Auto
Note on C296: 0 = Off 1 = Manual 2 = Auto
Note on N296: 1 = Off 2 = Manual 3 = Auto
Note on C297: 0 = Off 1 = Manual 2 = Auto
Note on N297: 1 = Off 2 = Manual 3 = Auto
Note on C298: 0 = Off 1 = Manual 2 = Auto
Note on C299: 0 = Off 1 = Manual 2 = Auto
Note on N299: 1 = Off 2 = Manual 3 = Auto
Note on C300: 0 = Off 1 = Manual 2 = Auto
Note on N300: 1 = Off 2 = Manual 3 = Auto
Note on C301: 0 = Off 1 = Manual 2 = Auto
Note on N301: 1 = Off 2 = Manual 3 = Auto
Note on C302: 0 = Off 1 = Manual 2 = Auto
Note on N302: 1 = Off 2 = Manual 3 = Auto
Note on C303: 0 = Off 1 = Manual 2 = Auto
Note on N303: 1 = Off 2 = Manual 3 = Auto
Note on C304: 0 = Off 1 = Manual 2 = Auto
Note on N304: 1 = Off 2 = Manual 3 = Auto
Note on C305: 0 = Off 1 = Manual 2 = Auto
Note on N305: 1 = Off 2 = Manual 3 = Auto
Note on C306: 0 = Off 1 = Manual 2 = Auto
Note on C312: 0 = Never 1 = Regularly 2 = Regularly and power up 3 = Regularly and power up and state change to Occupied
Note on C338: 0 = Actual temperature 1 = Heat setpoint 2 = Cool setpoint 3 = Average value of heating and cooling setpoint 4 = Setpoint offset 5 = CO2 level 6 = Heat setpoint + offset 7 = Cool setpoint + offset 8 = Average setpoint + offset 9 = Calculated air flow 10 = Active setpoint + offset
Note on N338: 1 = Actual temperature 2 = Heat setpoint 3 = Cool setpoint 4 = Average value of heating and cooling setpoint 5 = Setpoint offset 6 = CO2 level 7 = Heat setpoint + offset 8 = Cool setpoint + offset 9 = Average setpoint + offset 10 = Calculated air flow 11 = Active setpoint + offset
Note on C339: 0 = Setpoint offset 1 = Active setpoint + offset 2 = Heat setpoint + offset 3 = Cool setpoint + offset 4 = Heat occupied setpoint + offset 5 = Cool occupied setpoint + offset 6 = Average setpoint + offset
Note on N339: 1 = Setpoint offset 2 = Active setpoint + offset 3 = Heat setpoint + offset 4 = Cool setpoint + offset 5 = Heat occupied setpoint + offset 6 = Cool occupied setpoint + offset 7 = Average setpoint + offset
Note on C340: 0 = Off 1 = Manual 2 = Auto
Note on N340: 1 = Off 2 = Manual 3 = Auto
Note on C341: 0 = Off 1 = Manual 2 = Auto
Note on N341: 1 = Off 2 = Manual 3 = Auto
Note on C342: 0 = Off 1 = Manual 2 = Auto
Note on N342: 1 = Off 2 = Manual 3 = Auto
Note on C343: 0 = Off 1 = Manual 2 = Auto
Note on N343: 1 = Off 2 = Manual 3 = Auto
Note on C344: 0 = Off 1 = Manual 2 = Auto
Note on N344: 1 = Off 2 = Manual 3 = Auto
Note on C345: 0 = Off 1 = Manual 2 = Auto
Note on N345: 1 = Off 2 = Manual 3 = Auto
Note on C346: 0 = Off 1 = Manual 2 = Auto
Note on N346: 1 = Off 2 = Manual 3 = Auto
Note on C347: 0 = Off 1 = Manual 2 = Auto
Note on N347: 1 = Off 2 = Manual 3 = Auto
Note on C348: 0 = Off 1 = Manual 2 = Auto
Note on N348: 1 = Off 2 = Manual 3 = Auto
Note on C349: 0 = Off 1 = Manual 2 = Auto
Note on N349: 1 = Off 2 = Manual 3 = Auto
Note on C350: 0 = Off 1 = Manual 2 = Auto
Note on N350: 1 = Off 2 = Manual 3 = Auto
Note on C351: 0 = Off 1 = Manual 2 = Auto
Note on N351: 1 = Off 2 = Manual 3 = Auto
Note on C352: 0 = Off 1 = Manual 2 = Auto
Note on N352: 1 = Off 2 = Manual 3 = Auto
Note on C353: 0 = Off 1 = Manual 2 = Auto
Note on C354: 0 = Off 1 = Manual 2 = Auto
Note on N354: 1 = Off 2 = Manual 3 = Auto
Note on C355: 0 = Off 1 = Manual 2 = Auto
Note on C356: 0 = Off 1 = Manual 2 = Auto
Note on N356: 1 = Off 2 = Manual 3 = Auto
Note on C357: 0 = Off 1 = Manual 2 = Auto
Note on N357: 1 = Off 2 = Manual 3 = Auto
Note on C375: 0 = Always off 1 = Show only when the value is displayed 2 = Always on
Note on C385: 0 = Off 1 = Manual 2 = Auto
Note on N385: 1 = Off 2 = Manual 3 = Auto
Note on C386: 0 = Off 1 = Manual 2 = Auto
Note on N386: 1 = Off 2 = Manual 3 = Auto
Note on C387: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on N387: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on C397: 0 = Off 1 = Dehumidify 2 = Humidify
Note on C400: 0 = Off 1 = Dehumidify 2 = Humidify
Note on C401: 0 = Heating 1 = Cooling 2 = Auto
Note on C410: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C411: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C429: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C430: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C448: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C449: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C466: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C467: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C483: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C484: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C500: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C501: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C517: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C518: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C534: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C535: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C552: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C553: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C568: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C569: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C584: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C585: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C601: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C611: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C621: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C631: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C639: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C640: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V 10 = 0 = 0V, 10 = 10V 11 = 0 = 0mA, 20 = 20mA 12 = 0 = 0mA, 0.02 = 20mA
Note on C654: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C655: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V 10 = 0 = 0V, 10 = 10V 11 = 0 = 0mA, 20 = 20mA 12 = 0 = 0mA, 0.02 = 20mA
Note on C669: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C670: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V 10 = 0 = 0V, 10 = 10V 11 = 0 = 0mA, 20 = 20mA 12 = 0 = 0mA, 0.02 = 20mA
Note on C684: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C685: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V 10 = 0 = 0V, 10 = 10V 11 = 0 = 0mA, 20 = 20mA 12 = 0 = 0mA, 0.02 = 20mA
Note on C699: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C706: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C713: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C723: 0 = Do not display any boot screen 1 = Display device type 2 = Display device type and model 3 = Display device type, model and version 4 = Display device type, model, version and addresses
Note on C724: 0 = Adapt font to fit on screen, use as large as possible, if it does not fit, use scrolling and smalest font 1 = 5 pixels high font 2 = 7 pixels high font 3 = 10 pixels high font
Note on C725: 0 = Show only one row of text 1 = Show two rows of text
Note on C726: 0 = Wrap text at the end 1 = Bounce between start and end position 2 = Wrap text at the end, sync row 1 and 2 3 = Bounce between start and end position, sync row 1 and 2
Note on C728: 0 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 1 = Force display until remaining time is 0 2 = Show as a menu item as long as text is not empty
Note on C732: 0 = Disabled 1 = Enabled 2 = Read only
Note on C733: 0 = Disabled 1 = Enabled 2 = Read only
Note on C734: 0 = Disabled 1 = Enabled 2 = Read only
Note on C735: 0 = Disabled 1 = Enabled 2 = Read only
Note on C736: 0 = Disabled 1 = Enabled 2 = Read only
Note on C737: 0 = Disabled 1 = Enabled 2 = Read only
Note on C738: 0 = Disabled 1 = Enabled 2 = Read only
Note on C758: 0 = Disabled 1 = Enabled 2 = Read only
Note on C807: 0 = Inactive 2 = EXOline slave 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on C808: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on C810: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s