## Variables
PDTN - Variable list - ver. 1.0-1-01 | [17 empty] | Revision: | A
|  |  |  | EXOline |  |  | Modbus | [6 empty] | BACnet
Name | Default | Storage | Description | Type | Load | Cell | Reg. Type | RW | Register | Addr | Data Type | Scale | Offset | Default BACnet name | Object type | Instance | Unit | Writeable | Variable type
ModbusListVersion |  | RO | Modbus list version | X | 1 | 0 | Input | R | 300001 | 0 | U8
product_reset | 0 |  | Write to this register will trigger resets with different reset reasons | I | 1 | 1
rc_wink | 0 |  | Wink for this amount of time in seconds | X | 1 | 3 | Holding | RW | 400003 | 2 | U8 |  |  | Wink | positive_integer_value | 9011 |  | X
RC_CommSettingsCommit | 0 |  | Commit communication settings, set to 1 to commit port settings | L | 1 | 5 | Coil | RW | 000001 | 0 | LOGIC |  |  | CommCommit | binary_value | 9001 |  | X
RC_Port1Mode | 2 |  | Comm. protocol Port 1 (RS485) | X | 1 | 6 | Holding | RW | 400005 | 4 | U8 |  |  | Port1Mode | multi_state_value | 9001 |  | X
RC_Port1Baud | 0 |  | Comm. speed Port 1 (RS485) | X | 1 | 7 | Holding | RW | 400007 | 6 | U8 |  |  | Port1Baud | multi_state_value | 9101 |  | X
RC_Port1Format | 112 |  | Comm. format Port 1 (RS485) | X | 1 | 8 | Holding | RW | 400006 | 5 | U8 |  |  | Port1Format | multi_state_value | 9201 |  | X
SerialHigh |  | RO | Serial number, high part | I | 1 | 15 | Input | R | 300005 | 4 | I16
SerialMid |  | RO | Serial number, mid part | I | 1 | 17 | Input | R | 300004 | 3 | I16
SerialLow |  | RO | Serial number, low part | I | 1 | 19 | Input | R | 300003 | 2 | I16
RgbEnable | 0 |  | Set to True to enable the external control of the LED | L | 1 | 35 | Coil | RW | 000003 | 2 | LOGIC
RgbOffColor | 0 | CONF | 8 bit color for when the LED is in state Off (0bRRRGGGBB) | X | 1 | 36 | Holding | RW | 400027 | 26 | U8
RgbOffTime | 500 | CONF | Off time in ms | I | 1 | 37 | Holding | RW | 400028 | 27 | I16
RgbOnColor | 252 | CONF | 8 bit color for when the LED is in state On (0bRRRGGGBB) | X | 1 | 39 | Holding | RW | 400029 | 28 | U8
RgbOnTime | 100 | CONF | On time in ms | I | 1 | 40 | Holding | RW | 400030 | 29 | I16
product_status | 0 | RO | Bit field, See Description on Global device Status | I | 1 | 58 | Holding | RW | 400004 | 3 | I16
RafosVerMajor |  | RO | Platform software version, major part | X | 1 | 64 | Input | R | 300013 | 12 | U8
RafosVerMinor |  | RO | Platform software version, minor part | X | 1 | 65 | Input | R | 300014 | 13 | U8
RafosVerBranch |  | RO | Platform software version, branch part | X | 1 | 66 | Input | R | 300015 | 14 | U8
RafosVerNumber |  | RO | Platform software version, number part | X | 1 | 67 | Input | R | 300016 | 15 | U8
RafosGitCommit |  | RO | Platform Git commit | I | 1 | 68 | Input | R | 300017 | 16 | I16
OsId |  | RO | Application OPERATING_SYSTEM_ID | I | 1 | 70 | Input | R | 300021 | 20 | I16
VersionNumberString |  | RO | The application version as a string | $ | 1 | 76
gitCommitHashString |  | RO | The Full Git hash of the application | $ | 1 | 79
BleButtonMode | 2 | CONF | Function for BLE button | X | 1 | 83 | Holding | RW | 400071 | 70 | U8
BleButtonTimeout | 1800 | CONF | Timeout when BLE is started with the button | I | 1 | 84 | Holding | RW | 400072 | 71 | I16
BleVerMajor |  | RO | BLE stack version, major part | X | 1 | 98 | Input | R | 300022 | 21 | U8
BleVerMinor |  | RO | BLE stack version, minor part | X | 1 | 99 | Input | R | 300023 | 22 | U8
BleVerBranch |  | RO | BLE stack version, branch part | X | 1 | 100 | Input | R | 300024 | 23 | U8
BleVerNumber |  | RO | BLE stack version, number part | X | 1 | 101 | Input | R | 300025 | 24 | U8
FusVerMajor |  | RO | FUS stack version, major part | X | 1 | 102 | Input | R | 300026 | 25 | U8
FusVerMinor |  | RO | FUS version, minor part | X | 1 | 103 | Input | R | 300027 | 26 | U8
FusVerBranch |  | RO | FUS version, branch part | X | 1 | 104 | Input | R | 300028 | 27 | U8
FusVerNumber |  | RO | FUS version, number part | X | 1 | 105 | Input | R | 300029 | 28 | U8
ble_power | 35 | CONF | BLE TX power level | X | 1 | 108 | Holding | RW | 400082 | 81 | U8
disable_nv_storage | 0 | CONF | Set to 1 to disable storage in non volatile memory | L | 1 | 109 | Coil | RW | 000005 | 4 | LOGIC
IoAnaIn_4_mode | 128 | CONF | This variable configures the sensor mode, must be set to 128 to enable the sensor, set to 0 to disable the sensor and set all outputs to 0. | X | 4 | 153 | Holding | RW | 401076 | 1075 | U8
IoAnaIn_4_override | 0 | CONF | Override value | R | 4 | 179 | Holding | RW | 401089 401090 | 1088 1089 | REGx2I32SO | 100 | 0 | Pressure_1_override | analog_value | 1104 |  | X
IoAnaIn_4_override_en | 0 | CONF | Set to 1 to enable override | L | 4 | 182 | Coil | RW | 001076 | 1075 | LOGIC |  |  | Pressure_1_override_en | binary_value | 1004 |  | X
IoAnaIn_4_error |  | RO | Flag indicating any fault for signal | L | 4 | 183 | Discrete | R | 101076 | 1075 | LOGIC
IoAnaIn_4_errorFlags | 0 | RO | Detailed fault description | H | 4 | 184 | Holding | RW | 401091 401092 | 1090 1091 | REGx2I32
IoAnaIn_4_filter | 5 | CONF | Pressure sensor 1: Filter time (0 to 17200 seconds) | I | 4 | 187 | Holding | RW | 401093 | 1092 | I16
IoAnaIn_5_mode | 128 | CONF | This variable configures the sensor mode, must be set to 128 to enable the sensor, set to 0 to disable the sensor and set all outputs to 0. | X | 4 | 203 | Holding | RW | 401101 | 1100 | U8
IoAnaIn_5_override | 0 | CONF | Override value | R | 4 | 229 | Holding | RW | 401114 401115 | 1113 1114 | REGx2I32SO | 100 | 0 | Pressure_2_override | analog_value | 1105 |  | X
IoAnaIn_5_override_en | 0 | CONF | Set to 1 to enable override | L | 4 | 232 | Coil | RW | 001101 | 1100 | LOGIC |  |  | Pressure_2_override_en | binary_value | 1005 |  | X
IoAnaIn_5_error |  | RO | Flag indicating any fault for signal | L | 4 | 233 | Discrete | R | 101101 | 1100 | LOGIC
IoAnaIn_5_errorFlags | 0 | RO | Detailed fault description | H | 4 | 234 | Holding | RW | 401116 401117 | 1115 1116 | REGx2I32
IoAnaIn_5_filter | 5 | CONF | Pressure sensor 2: Filter time (0 to 17200 seconds) | I | 4 | 237 | Holding | RW | 401118 | 1117 | I16
IoAnaOut_1_value | 0 |  | Value in % set for output | R | 5 | 0 | Holding | RW | 402501 | 2500 | I16SO | 100 | 0 | Output_Channel_1_value | analog_value | 1201 | percent | X
IoAnaOut_1_mode | 1 | CONF | Mode for output | X | 5 | 3 | Holding | RW | 402502 | 2501 | U8
IoAnaOut_1_unit | 0 | CONF | Unit converter | X | 5 | 4 | Holding | RW | 402503 | 2502 | U8
IoAnaOut_1_min_in | 0 | CONF | Scale for output | R | 5 | 5 | Holding | RW | 402504 | 2503 | I16SO | 100 | 0
IoAnaOut_1_min_out | 0 | CONF | Scale for output | R | 5 | 8 | Holding | RW | 402505 | 2504 | I16SO | 100 | 0
IoAnaOut_1_max_in | 100 | CONF | Scale for output | R | 5 | 11 | Holding | RW | 402506 | 2505 | I16SO | 100 | 0
IoAnaOut_1_max_out | 100 | CONF | Scale for output | R | 5 | 14 | Holding | RW | 402507 | 2506 | I16SO | 100 | 0
IoAnaOut_1_offset | 0 | CONF | Offset for output | R | 5 | 17 | Holding | RW | 402508 | 2507 | I16SO | 100 | 0
IoAnaOut_1_default | 0 | CONF | Default value if communication is lost | R | 5 | 20 | Holding | RW | 402509 | 2508 | I16SO | 100 | 0 | Output_Channel_1_default | analog_value | 1301 | percent | X
IoAnaOut_1_converted |  | RO | Actual value on the output pin in Volt or milliampere. | R | 5 | 23 | Input | R | 302501 | 2500 | I16SO | 100 | 0 | Output_Channel_1_converted | analog_value | 1401 | volts
IoAnaOut_1_raw |  | RO | Raw value sent to HW | R | 5 | 26 | Input | R | 302502 | 2501 | I16SO | 100 | 0
IoAnaOut_1_override | 0 | CONF | Override value | R | 5 | 29 | Holding | RW | 402510 | 2509 | I16SO | 100 | 0 | Output_Channel_1_override | analog_value | 1501 | percent | X
IoAnaOut_1_override_en | 0 | CONF | Set to 1 to enable override | L | 5 | 32 | Coil | RW | 002501 | 2500 | LOGIC |  |  | Output_Channel_1_override_en | binary_value | 1401 |  | X
IoAnaOut_1_ramp | 0 | CONF | Limits the change in output to this value in units (%?) / s. A value of 0 means that the output will not be limited. | R | 5 | 33 | Holding | RW | 402511 | 2510 | I16SO | 100 | 0
IoAnaOut_1_pulse_period | 60 | CONF | Period time for pulse output | I | 5 | 36 | Holding | RW | 402512 | 2511 | I16
IoAnaOut_2_value | 0 |  | Value in % set for output | R | 5 | 50 | Holding | RW | 402526 | 2525 | I16SO | 100 | 0 | Output_Channel_2_value | analog_value | 1202 | percent | X
IoAnaOut_2_mode | 1 | CONF | Mode for output | X | 5 | 53 | Holding | RW | 402527 | 2526 | U8
IoAnaOut_2_unit | 0 | CONF | Unit converter | X | 5 | 54 | Holding | RW | 402528 | 2527 | U8
IoAnaOut_2_min_in | 0 | CONF | Scale for output | R | 5 | 55 | Holding | RW | 402529 | 2528 | I16SO | 100 | 0
IoAnaOut_2_min_out | 0 | CONF | Scale for output | R | 5 | 58 | Holding | RW | 402530 | 2529 | I16SO | 100 | 0
IoAnaOut_2_max_in | 100 | CONF | Scale for output | R | 5 | 61 | Holding | RW | 402531 | 2530 | I16SO | 100 | 0
IoAnaOut_2_max_out | 100 | CONF | Scale for output | R | 5 | 64 | Holding | RW | 402532 | 2531 | I16SO | 100 | 0
IoAnaOut_2_offset | 0 | CONF | Offset for output | R | 5 | 67 | Holding | RW | 402533 | 2532 | I16SO | 100 | 0
IoAnaOut_2_default | 0 | CONF | Default value if communication is lost | R | 5 | 70 | Holding | RW | 402534 | 2533 | I16SO | 100 | 0 | Output_Channel_2_default | analog_value | 1302 | percent | X
IoAnaOut_2_converted |  | RO | Actual value on the output pin in Volt or milliampere. | R | 5 | 73 | Input | R | 302526 | 2525 | I16SO | 100 | 0 | Output_Channel_2_converted | analog_value | 1402 | volts
IoAnaOut_2_raw |  | RO | Raw value sent to HW | R | 5 | 76 | Input | R | 302527 | 2526 | I16SO | 100 | 0
IoAnaOut_2_override | 0 | CONF | Override value | R | 5 | 79 | Holding | RW | 402535 | 2534 | I16SO | 100 | 0 | Output_Channel_2_override | analog_value | 1502 | percent | X
IoAnaOut_2_override_en | 0 | CONF | Set to 1 to enable override | L | 5 | 82 | Coil | RW | 002526 | 2525 | LOGIC |  |  | Output_Channel_2_override_en | binary_value | 1402 |  | X
IoAnaOut_2_ramp | 0 | CONF | Limits the change in output to this value in units (%?) / s. A value of 0 means that the output will not be limited. | R | 5 | 83 | Holding | RW | 402536 | 2535 | I16SO | 100 | 0
IoAnaOut_2_pulse_period | 60 | CONF | Period time for pulse output | I | 5 | 86 | Holding | RW | 402537 | 2536 | I16
Disp_BrightnessFull | 100 | CONF | Display brightness, full (%) | X | 6 | 0 | Holding | RW | 406001 | 6000 | U8 |  |  | Disp_BrightnessFull | analog_value | 8001 | percent | X
Disp_BrightnessDim | 20 | CONF | Display brightness, dimmed (%) | X | 6 | 1 | Holding | RW | 406002 | 6001 | U8 |  |  | Disp_BrightnessDim | analog_value | 8011 | percent | X
Disp_TimeFull | 0 | CONF | Display time in full mode. 0 = Never dim. | I | 6 | 2 | Holding | RW | 406003 | 6002 | I16 |  |  | Disp_TimeFull | analog_value | 8021 | seconds | X
Disp_TimeDim | 30 | CONF | Display time in dimmed mode. 0 = Never off. | I | 6 | 4 | Holding | RW | 406004 | 6003 | I16 |  |  | Disp_TimeDim | analog_value | 8031 | seconds | X
DisplayStartupMode | 4 | CONF | What to display during device startup | X | 6 | 8 | Holding | RW | 406005 | 6004 | U8
applicationForceOff | 0 | CONF | Set to 1 to disable all application functions | X | 10 | 0 | Holding | RW | 407001 | 7000 | U8
PS_display_value_time_ms | 3500 | CONF | This is the time in milliseconds (ms) that the value is shown in the display, before alternating to the unit. | I | 10 | 1 | Holding | RW | 407002 | 7001 | I16 |  |  | PS_display_value_time_ms | positive_integer_value | 10004 | milliseconds | X
PS_display_unit_time_ms | 1000 | CONF | This is the time in milliseconds (ms) that the unit is shown in the display, before alternating to the value. | I | 10 | 3 | Holding | RW | 407003 | 7002 | I16 |  |  | PS_display_unit_time_ms | positive_integer_value | 10005 | milliseconds | X
PS_display_split_time_ms | 1000 | CONF | This is the time in milliseconds (ms) that the display is off between alternating to a new channel. This is only valid in single row display mode. | I | 10 | 5 | Holding | RW | 407004 | 7003 | I16 |  |  | PS_display_split_time_ms | positive_integer_value | 10006 | milliseconds | X
PS_display_mode | 0 | CONF | Used to set the display layout. | X | 10 | 7 | Holding | RW | 407005 | 7004 | U8 |  |  | PS_display_mode | multi_state_value | 10000 |  | X
PS_display_channel_time_ms | 1000 | CONF | This is the time in milliseconds (ms) that the channel is shown in the display before showing the value. This is only valid in single row display mode | I | 10 | 8 | Holding | RW | 407006 | 7005 | I16 |  |  | PS_display_channel_time_ms | positive_integer_value | 10007 | milliseconds | X
PS_display_text_time_ms | 0 | CONF | This is the time in milliseconds (ms) that the custom text is shown in the display, before alternating to the channel value. | H | 10 | 10 | Holding | RW | 407007 407008 | 7006 7007 | REGx2I32 |  |  | PS_display_text_time_ms | positive_integer_value | 10008 | milliseconds | X
PS_display_text_font | 0 | CONF | What font to use for the display text | X | 10 | 13 | Holding | RW | 407009 | 7008 | U8 |  |  | ps_text_font | multi_state_value | 11000 |  | X
PS_display_text_scroll_mode | 0 | CONF | Scroll mode | X | 10 | 14 | Holding | RW | 407010 | 7009 | U8 |  |  | PS_display_text_scroll_mode | multi_state_value | 11001 |  | X
PS_display_text_replace_chn_tag | 0 | CONF | In single row, replace the CHx tag with this text | L | 10 | 15 | Coil | RW | 007001 | 7000 | LOGIC |  |  | PS_display_text_replace_chn_tag | binary_value | 10003 |  | X
PS_display_text_scroll_speed | 100 | CONF | Time in ms between scrolling one pixel | I | 10 | 16 | Holding | RW | 407011 | 7010 | I16 |  |  | PS_display_text_scroll_speed | analog_value | 11000 | milliseconds | X
AdaptTimeDisp_ACTIVATE | 0 | CONF | Adaptive Time for Display: Activate the adaptive time display for single row displays | L | 10 | 50 | Coil | RW | 007002 | 7001 | LOGIC |  |  | Adaptive_Display_Time | binary_value | 10000 |  | X
AdaptTimeDisp_DUTY | 0.5 | RO | Adaptive Time for Display: Current calculated duty between channels. | R | 10 | 51 | Holding | RW | 407012 407013 | 7011 7012 | REGx2I32SO | 10000 | 0
AdaptTimeDisp_MIN_ONTime | 500 | CONF | Adaptive Time for Display: minimum on per view, e.g., 500 ms | H | 10 | 54 | Holding | RW | 407014 407015 | 7013 7014 | REGx2I32
AdaptTimeDisp_QUIET_HOLD | 2000 | CONF | Adaptive Time for Display: Holdoff for quite detection | H | 10 | 57 | Holding | RW | 407016 407017 | 7015 7016 | REGx2I32
AdaptTimeDisp_CR_ch1 | 0 | RO | Adaptive Time for Display: Change rate for channel. | R | 10 | 60 | Holding | RW | 407018 407019 | 7017 7018 | REGx2I32SO | 10000 | 0
AdaptTimeDisp_CR_ch2 | 0 | RO | Adaptive Time for Display: Change rate for channel. | R | 10 | 63 | Holding | RW | 407020 407021 | 7019 7020 | REGx2I32SO | 10000 | 0
AdaptTimeDisp_DUTY_ALPHA | 0.1 | CONF | Adaptive Time for Display: EWMA smoothing factor for change-rate, e.g., 0.0005..0.02 | R | 10 | 66 | Holding | RW | 407022 407023 | 7021 7022 | REGx2I32SO | 10000 | 0
AdaptTimeDisp_DutySlope | 0.025 | CONF | Adaptive Time for Display: Max change per cycle for duty | R | 10 | 69 | Holding | RW | 407024 407025 | 7023 7024 | REGx2I32SO | 10000 | 0
AdaptTimeDisp_FLOOR | 0.7 | CONF | Adaptive Time for Display: ignore changes below this level | R | 10 | 72 | Holding | RW | 407026 407027 | 7025 7026 | REGx2I32SO | 10000 | 0
AdaptTimeDisp_TAU_FAST | 1 | CONF | Adaptive Time for Display: fast EMA [s] | R | 10 | 75 | Holding | RW | 407028 407029 | 7027 7028 | REGx2I32SO | 10000 | 0
AdaptTimeDisp_TAU_INT | 3 | CONF | Adaptive Time for Display: leaky integrator [s] | R | 10 | 78 | Holding | RW | 407030 407031 | 7029 7030 | REGx2I32SO | 10000 | 0
AdaptTimeDisp_TAU_SLOW | 8 | CONF | Adaptive Time for Display: slow EMA [s] | R | 10 | 81 | Holding | RW | 407032 407033 | 7031 7032 | REGx2I32SO | 10000 | 0
AdaptTimeDisp_QUIET | 0.5 | CONF | Adaptive Time for Display: Quite threshold | R | 10 | 84 | Holding | RW | 407034 407035 | 7033 7034 | REGx2I32SO | 10000 | 0
AdaptTimeDisp_P | 1.5 | CONF | Adaptive Time for Display: nonlinearity, e.g., 1.0 (linear) or 1.5..2.0 to accentuate differences | R | 10 | 87 | Holding | RW | 407036 407037 | 7035 7036 | REGx2I32SO | 10000 | 0
PS_1_range | 9 | CONF | Range Selected by switch, set to value outside of switch range to use custom mapping, set value to 20 to disable mapping | X | 10 | 100 | Holding | RW | 407038 | 7037 | U8 |  |  | PS_1_range | multi_state_value | 10001 |  | X
PS_1_pressure |  | RO | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. | R | 10 | 101 | Input | R | 307001 307002 | 7000 7001 | REGx2I32SO | 10000 | 0 | PS_1_pressure | analog_value | 10002
PS_1_pressure_scaled |  | RO | This variable contains the current pressure in the unit selected by the PSx_UNIT variable, but is not represented as a float number. It is an integer between -32768 and 32767 that needs to be scaled depending on the selected unit. (The main reason for this variable is to make the value fit into a single Modbus register) For Pascal [Pa], take the value and divide by 4. For kilo Pascal [Pa], take the value and divide by 4000. For PSI, take the value and divide by 20000. For millibar [mBar], take the value and divide by 400. For inches of water column [inch H2O], take the value and divide by 1000. For millimeter of water column [mm H2O], take the value and divide by 40 | I | 10 | 106 | Input | R | 307003 | 7002 | I16
PS_1_flow |  | RO | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA | R | 10 | 108 | Input | R | 307004 307005 | 7003 7004 | REGx2I32SO | 1000 | 0 | PS_1_flow | analog_value | 10004
PS_1_flow_scaled |  | RO | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. but is is not represented as a float number. It is an integer between -32768 and 32767 that needs to be scaled depending on the selected unit. (The main reason for this variable is to make the value fit into a single Modbus register) For cubic meters per hour [m3/h], take the value and multiply by 4. For cubic meters per second [m3/s], take the value and divide by 1000. For litres per second [l/s], take the value as is. For cubic feet per minute [CFM], take the value and multiply by two. | I | 10 | 111 | Input | R | 307006 | 7005 | I16
PS_1_unit | 0 | CONF | Used to convert the pressure sensor output value to the preferred unit | X | 10 | 113 | Holding | RW | 407039 | 7038 | U8 |  |  | PS_1_unit | multi_state_value | 10003 |  | X
PS_1_flow_unit | 0 | CONF | Used to convert the pressure sensor output value to the preferred unit. | X | 10 | 114 | Holding | RW | 407040 | 7039 | U8 |  |  | PS_1_flow_unit | multi_state_value | 10005 |  | X
PS_1_flow_formula | 0 | CONF | The formula used to calculate the flow from the measured pressure | X | 10 | 115 | Holding | RW | 407041 | 7040 | U8 |  |  | PS_1_flow_formula | multi_state_value | 10007 |  | X
PS_1_flow_k_factor | 5 | CONF | The K factor used in the flow calculation | R | 10 | 116 | Holding | RW | 407042 407043 | 7041 7042 | REGx2I32SO | 1000 | 0 | PS_1_flow_k_factor | analog_value | 10006 |  | X
PS_1_flow_air_density | 1.205 | CONF | Air density used on some flow calculations | R | 10 | 119 | Holding | RW | 407044 407045 | 7043 7044 | REGx2I32SO | 10000 | 0 | PS_1_flow_air_density | analog_value | 10008 |  | X
PS_1_display_unit | 1 | CONF | Used to set the displayed value in the display | X | 10 | 122 | Holding | RW | 407046 | 7045 | U8 |  |  | PS_1_display_unit | multi_state_value | 10009 |  | X
PS_1_display_value |  | RO | Used to read the value currently displayed | R | 10 | 123 | Input | R | 307007 307008 | 7006 7007 | REGx2I32SO | 10000 | 0 | PS_1_display_value | analog_value | 10010
PS_1_MaxPressure |  | RO | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor | I | 10 | 126 | Input | R | 307009 | 7008 | I16 |  |  | PS_1_MaxPressure | analog_value | 10012 | pascals
PS_1_MinPressure |  | RO | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor | I | 10 | 128 | Input | R | 307010 | 7009 | I16 |  |  | PS_1_MinPressure | analog_value | 10014 | pascals
PS_1_display_resolution | 0.1 | CONF | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. | R | 10 | 130 | Holding | RW | 407047 407048 | 7046 7047 | REGx2I32SO | 1000 | 0 | PS_1_display_resolution | analog_value | 10016 |  | X
PS_1_resolution | 0.01 | CONF | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy | R | 10 | 133 | Holding | RW | 407049 407050 | 7048 7049 | REGx2I32SO | 1000 | 0 | PS_1_resolution | analog_value | 10018 |  | X
PS_1_display_extra_unit | 0 | CONF | Used to set an additional value to be displayed for this channel. | X | 10 | 136 | Holding | RW | 407051 | 7050 | U8 |  |  | PS_1_display_extra_unit | multi_state_value | 10011 |  | X
PS_1_display_extra_value |  | RO | Used to read the value currently displayed extra value | R | 10 | 137 | Input | R | 307011 307012 | 7010 7011 | REGx2I32SO | 10000 | 0 | PS_1_display_extra_value | analog_value | 10020 |  | X
PS_1_MapMaxPressure | 0 | CONF | Used for custom Mapping och analog output range | R | 10 | 140 | Holding | RW | 407052 407053 | 7051 7052 | REGx2I32SO | 1000 | 0 | PS_1_MapMaxPressure | analog_value | 10022 |  | X
PS_1_MapMinPressure | 0 | CONF | Used for custom Mapping och analog output range | R | 10 | 143 | Holding | RW | 407054 407055 | 7053 7054 | REGx2I32SO | 1000 | 0 | PS_1_MapMinPressure | analog_value | 10024 |  | X
PS_1_set_zero | 0 |  | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. | L | 10 | 146 | Coil | RW | 007003 | 7002 | LOGIC |  |  | PS_1_set_zero | binary_value | 10001 |  | X
PS_1_text_row |  | CONF | String to show on row 1 in the display | $ | 10 | 147 | Holding | RW | 407056 - 407087 | 7055 - 7086 | STRING |  |  | PS_1_text_row | characterstring_value | 11000 |  | X
PS_2_range | 9 | CONF | Range Selected by switch, set to value outside of switch range to use custom mapping, set value to 20 to disable mapping | X | 10 | 200 | Holding | RW | 407088 | 7087 | U8 |  |  | PS_2_range | multi_state_value | 10002 |  | X
PS_2_pressure |  | RO | This variable contains the current pressure in the unit selected by the PSx_UNIT variable. The value is filtered by the IoAnaIn_4_filter/IoAnaIn_5_filter setting. To enable the pressure sensor the PSx_MODE must be set to 128. The resolution can be limited by setting the PSx_RESOLUTION variable, useful to get rid of small changes and noise. | R | 10 | 201 | Input | R | 307013 307014 | 7012 7013 | REGx2I32SO | 10000 | 0 | PS_2_pressure | analog_value | 10003
PS_2_pressure_scaled |  | RO | This variable contains the current pressure in the unit selected by the PSx_UNIT variable, but is not represented as a float number. It is an integer between -32768 and 32767 that needs to be scaled depending on the selected unit. (The main reason for this variable is to make the value fit into a single Modbus register) For Pascal [Pa], take the value and divide by 4. For kilo Pascal [Pa], take the value and divide by 4000. For PSI, take the value and divide by 20000. For millibar [mBar], take the value and divide by 400. For inches of water column [inch H2O], take the value and divide by 1000. For millimeter of water column [mm H2O], take the value and divide by 40 | I | 10 | 206 | Input | R | 307015 | 7014 | I16
PS_2_flow |  | RO | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. The value is based on the PSx_PRESSURE value and all filtering and resolution settings are based on that. The flow calculation is based on the settings in PSx_FLOW_K_FACTOR, PSx_FLOW_AIR_DENSITY and PSx_FLOW_FORMULA | R | 10 | 208 | Input | R | 307016 307017 | 7015 7016 | REGx2I32SO | 1000 | 0 | PS_2_flow | analog_value | 10005
PS_2_flow_scaled |  | RO | This variable contains the current flow in the unit selected by the PSx_FLOW_UNIT variable. but is is not represented as a float number. It is an integer between -32768 and 32767 that needs to be scaled depending on the selected unit. (The main reason for this variable is to make the value fit into a single Modbus register) For cubic meters per hour [m3/h], take the value and multiply by 4. For cubic meters per second [m3/s], take the value and divide by 1000. For litres per second [l/s], take the value as is. For cubic feet per minute [CFM], take the value and multiply by two. | I | 10 | 211 | Input | R | 307018 | 7017 | I16
PS_2_unit | 0 | CONF | Used to convert the pressure sensor output value to the preferred unit | X | 10 | 213 | Holding | RW | 407089 | 7088 | U8 |  |  | PS_2_unit | multi_state_value | 10004 |  | X
PS_2_flow_unit | 0 | CONF | Used to convert the pressure sensor output value to the preferred unit. | X | 10 | 214 | Holding | RW | 407090 | 7089 | U8 |  |  | PS_2_flow_unit | multi_state_value | 10006 |  | X
PS_2_flow_formula | 0 | CONF | The formula used to calculate the flow from the measured pressure | X | 10 | 215 | Holding | RW | 407091 | 7090 | U8 |  |  | PS_2_flow_formula | multi_state_value | 10008 |  | X
PS_2_flow_k_factor | 5 | CONF | The K factor used in the flow calculation | R | 10 | 216 | Holding | RW | 407092 407093 | 7091 7092 | REGx2I32SO | 1000 | 0 | PS_2_flow_k_factor | analog_value | 10007 |  | X
PS_2_flow_air_density | 1.205 | CONF | Air density used on some flow calculations | R | 10 | 219 | Holding | RW | 407094 407095 | 7093 7094 | REGx2I32SO | 10000 | 0 | PS_2_flow_air_density | analog_value | 10009 |  | X
PS_2_display_unit | 1 | CONF | Used to set the displayed value in the display | X | 10 | 222 | Holding | RW | 407096 | 7095 | U8 |  |  | PS_2_display_unit | multi_state_value | 10010 |  | X
PS_2_display_value |  | RO | Used to read the value currently displayed | R | 10 | 223 | Input | R | 307019 307020 | 7018 7019 | REGx2I32SO | 10000 | 0 | PS_2_display_value | analog_value | 10011
PS_2_MaxPressure |  | RO | This variable contains maximum measurable pressure in Pascal [Pa] for the selected sensor | I | 10 | 226 | Input | R | 307021 | 7020 | I16 |  |  | PS_2_MaxPressure | analog_value | 10013 | pascals
PS_2_MinPressure |  | RO | This variable contains minimum measurable pressure in Pascal [Pa] for the selected sensor | I | 10 | 228 | Input | R | 307022 | 7021 | I16 |  |  | PS_2_MinPressure | analog_value | 10015 | pascals
PS_2_display_resolution | 0.1 | CONF | This variable contains the percentage of the sensor range to use as rounding of the value shown on the display. Default value is set to 0.1% as that is greater then the sensor accuracy. | R | 10 | 230 | Holding | RW | 407097 407098 | 7096 7097 | REGx2I32SO | 1000 | 0 | PS_2_display_resolution | analog_value | 10017 |  | X
PS_2_resolution | 0.01 | CONF | This variable contains the percentage of the sensor range to use as rounding of values for communication, default is set to 0.01% as that is greater then the sensor accuracy | R | 10 | 233 | Holding | RW | 407099 407100 | 7098 7099 | REGx2I32SO | 1000 | 0 | PS_2_resolution | analog_value | 10019 |  | X
PS_2_display_extra_unit | 0 | CONF | Used to set an additional value to be displayed for this channel. | X | 10 | 236 | Holding | RW | 407101 | 7100 | U8 |  |  | PS_2_display_extra_unit | multi_state_value | 10012 |  | X
PS_2_display_extra_value |  | RO | Used to read the value currently displayed extra value | R | 10 | 237 | Input | R | 307023 307024 | 7022 7023 | REGx2I32SO | 10000 | 0 | PS_2_display_extra_value | analog_value | 10021 |  | X
PS_2_MapMaxPressure | 0 | CONF | Used for custom Mapping och analog output range | R | 10 | 240 | Holding | RW | 407102 407103 | 7101 7102 | REGx2I32SO | 1000 | 0 | PS_2_MapMaxPressure | analog_value | 10023 |  | X
PS_2_MapMinPressure | 0 | CONF | Used for custom Mapping och analog output range | R | 10 | 243 | Holding | RW | 407104 407105 | 7103 7104 | REGx2I32SO | 1000 | 0 | PS_2_MapMinPressure | analog_value | 10025 |  | X
PS_2_set_zero | 0 |  | If a 1 is written to this register a zero calibration of the current sensor will be performed. Make sure the PSx_VALUE is stable and no pressure applied to the sensor before writing to this register. The value will be reset to 0 automatically when the zero calibration is done by the device. | L | 10 | 246 | Coil | RW | 007004 | 7003 | LOGIC |  |  | PS_2_set_zero | binary_value | 10002 |  | X
PS_2_text_row |  | CONF | String to show on row 2 in the display | $ | 10 | 247 | Holding | RW | 407106 - 407137 | 7105 - 7136 | STRING |  |  | PS_2_text_row | characterstring_value | 11001 |  | X
rt_fb_visability | 0 | CONF | When to show the custom frame buffer | X | 10 | 300 | Holding | RW | 400101 | 100 | U8 |  |  | rt_fb_visability | multi_state_value | 11002 |  | X
rt_fb_timeleft | 0 |  | Time to show the custom frame buffer | I | 10 | 301 | Holding | RW | 400102 | 101 | I16 |  |  | rt_fb_timeleft | analog_value | 11001 | seconds | X
rt_fb_row0 | 0 |  | Frame buffer data for row 0 on the display | H | 10 | 303 | Holding | RW | 400103 400104 | 102 103 | REGx2I32 |  |  | rt_fb_row0 | analog_value | 11002 |  | X
rt_fb_row1 | 0 |  | Frame buffer data for row 1 on the display | H | 10 | 306 | Holding | RW | 400105 400106 | 104 105 | REGx2I32 |  |  | rt_fb_row1 | analog_value | 11003 |  | X
rt_fb_row2 | 0 |  | Frame buffer data for row 2 on the display | H | 10 | 309 | Holding | RW | 400107 400108 | 106 107 | REGx2I32 |  |  | rt_fb_row2 | analog_value | 11004 |  | X
rt_fb_row3 | 0 |  | Frame buffer data for row 3 on the display | H | 10 | 312 | Holding | RW | 400109 400110 | 108 109 | REGx2I32 |  |  | rt_fb_row3 | analog_value | 11005 |  | X
rt_fb_row4 | 0 |  | Frame buffer data for row 4 on the display | H | 10 | 315 | Holding | RW | 400111 400112 | 110 111 | REGx2I32 |  |  | rt_fb_row4 | analog_value | 11006 |  | X
rt_fb_row5 | 0 |  | Frame buffer data for row 5 on the display | H | 10 | 318 | Holding | RW | 400113 400114 | 112 113 | REGx2I32 |  |  | rt_fb_row5 | analog_value | 11007 |  | X
rt_fb_row6 | 0 |  | Frame buffer data for row 6 on the display | H | 10 | 321 | Holding | RW | 400115 400116 | 114 115 | REGx2I32 |  |  | rt_fb_row6 | analog_value | 11008 |  | X
rt_fb_row7 | 0 |  | Frame buffer data for row 7 on the display | H | 10 | 324 | Holding | RW | 400117 400118 | 116 117 | REGx2I32 |  |  | rt_fb_row7 | analog_value | 11009 |  | X
rt_fb_row8 | 0 |  | Frame buffer data for row 8 on the display | H | 10 | 327 | Holding | RW | 400119 400120 | 118 119 | REGx2I32 |  |  | rt_fb_row8 | analog_value | 11010 |  | X
rt_fb_row9 | 0 |  | Frame buffer data for row 9 on the display | H | 10 | 330 | Holding | RW | 400121 400122 | 120 121 | REGx2I32 |  |  | rt_fb_row9 | analog_value | 11011 |  | X
rt_fb_row10 | 0 |  | Frame buffer data for row 10 on the display | H | 10 | 333 | Holding | RW | 400123 400124 | 122 123 | REGx2I32 |  |  | rt_fb_row10 | analog_value | 11012 |  | X
PLA | 242 | COM |  | X | 241 | 0
ELA | 1 | COM |  | X | 241 | 1
Ver_Minor |  | RO |  | X | 241 | 16 | Input | R | 300007 | 6 | U8
Ver_Major |  | RO |  | X | 241 | 17 | Input | R | 300006 | 5 | U8
MODEL_ALIAS |  | RO | Model number | I | 241 | 36 | Input | R | 300050 | 49 | I16
Model |  | RO | Model number | I | 241 | 36 | Input | R | 300002 | 1 | I16
Ver_Branch |  | RO |  | X | 241 | 40 | Input | R | 300008 | 7 | U8
Ver_Number |  | RO |  | X | 241 | 41 | Input | R | 300009 | 8 | U8
SerialNumberString | 0 | RO |  | $ | 241 | 60
ControllerName | PDTN | CONF | Device name, visible in App list | $ | 241 | 63 | Holding | RW | 400039 - 400070 | 38 - 69 | STRING
ControllerProject | 0 | CONF | Device project | $ | 241 | 66
ControllerDescription |  | CONF | Device description | $ | 241 | 69
ControllerLocation |  | CONF | Device location | $ | 241 | 72
UptimeMillisec | 0 | RO |  | I | 241 | 75
UptimeSec | 0 | RO |  | H | 241 | 77
GitCommit |  | RO | Internal revision number | I | 241 | 80 | Input | R | 300011 | 10 | I16
ModelName | 0 | RO |  | $ | 241 | 100
VendorName | AB Regin | RO |  | $ | 241 | 109
OSid |  | RO | Application OPERATING_SYSTEM_ID | H | 241 | 138
BACnetCommitSettings | 0 |  | Commit BACnet settings | L | 242 | 59
BACnetDeviceID | -1 | COM | BACnet device ID | H | 242 | 60
BACnetDeviceObjectName | PDTN | COM | BACnet device object name | $ | 242 | 63
BACnetSegmentationSupported | 3 | CONF | BACnet segmentation supported | X | 242 | 66
BACnetAPDUTimeout | 3000 | COM | BACnet APDU timeout | I | 242 | 67
BACnetAPDUsegmentTimeout | 2000 | COM | BACnet APDU segment timeout | I | 242 | 69
BACnetWideCharacterSetEncoding | 0 | CONF | BACnet wide character set encoding | X | 242 | 73
BACnetVendorName | AB Regin | CONF | BACnet vendor name | $ | 242 | 75
BACnetVendorIdentifier | 264 | CONF | BACnet vendor identifier | I | 242 | 78
BACnetMstpMAC_Port_1 | 0 | COM | BACnet MS/TP MAC port 1 | X | 242 | 85
BACnetMstpMaxAPDUlenAccepted_Port_1 | 480 | CONF | BACnet MS/TP max accepted APDU length port 1 | I | 242 | 86
BACnetMstpNrOfAPDUretries_Port_1 | 3 | COM | BACnet MS/TP no of APDU retries port 1 | X | 242 | 88
BACnetMstpMaxMasterAddr_Port_1 | 127 | CONF | BACnet MS/TP max master address port 1 | X | 242 | 89
BACnetMstpMaxInfoFrames_Port_1 | 1 | CONF | BACnet MS/TP max info frames port 1 | X | 242 | 90
BACnetMaxServerCOV | 100 | COM | BACnet max server COV | I | 242 | 135
BACnetPassword | 1111 | COM | BACnet password | $ | 242 | 139
BACnetDatabaseRevisionTicker | 0 | COM | BACnet database revision ticker | I | 242 | 142
ModbusUnitID | 1 | COM | Active Modbus unit ID | X | 242 | 172 | Holding | RW | 400002 | 1 | U8
ModbusCharTimeout_Port_1 | 3 | COM |  | I | 242 | 197 | Holding | RW | 400008 | 7 | I16
ModbusAnswerDelay_Port_1 | 5 | COM |  | I | 242 | 199 | Holding | RW | 400009 | 8 | I16
Mode_Port_1 | 2 | RO | Active RS485 port mode/protocol | X | 248 | 0
Format_Port_1 | 112 | RO | Active RS485 port format | X | 248 | 35
TimeOut_Port_1 | 0 | RO |  | X | 248 | 38
Baud_Port_1 | 0 | RO | Active RS485 port baud rate | X | 248 | 41
Note on C3: RO = Read only variable COM = Communication settings [Non volatile] CONF = Configuration settings [Non volatile]
Note on L3: LOGIC: Used for True/False values, only allowed for "Discrete inputs" and "Coils" U8: One 8 bit unsigned integer variable to/from LSB of one register I16: One 16 bit integer variable to/from one register I16SO: Floating point variable converted to 16 bit integer to/from one register. Scale and Offset used REGx2IEEE: First register: MSW of floating point variable to/from one 16-bit register (IEEE) Second register: LSW of floating point variable to/from one 16-bit register (IEEE) REGx2I32: First register: MSW of 32 bit integer variable to/from one 16-bit register Second register: LSW of 32 bit integer variable to/from one 16-bit register REGx2I32SO: First register: MSW of 32 bit integer converted from floating point variable. Scale & Offset used. R/O Second register: LSW of 32 bit integer converted from floating point variable. Scale & Offset used. R/O
Note on D5: 0 = Device running normally 23040 = Do nothing 23041 = Cools reset 23042 = Upgrade 23043 = Colds 23044 = Power up 23045 = Warm reset 23046 = Save config as user default 23047 = Restore config from user default 23048 = Switch to Bluetooth Direct Test Mode
Note on D8: 0 = Inactive 2 = EXOline slave 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on P8: 1 = Inactive 3 = EXOline slave 14 = BACnet 16 = Modbus slave 22 = EXOline/Modbus autodetect
Note on D9: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s
Note on P9: 1 = 9600 bits/s 3 = 2400 bits/s 4 = 1200 bits/s 16 = 19200 bits/s 18 = 38400 bits/s 19 = 57600 bits/s 21 = 115200 bits/s 22 = 230400 bits/s 23 = 460800 bits/s 26 = 921k6 bits/s 27 = 1000000 bits/s 28 = 250000 bits/s
Note on D10: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on P10: 17 = 8 bit, no parity, 1 stop bit 25 = 8 bit, no parity, 2 stop bits 49 = 8 bit, even parity, 1 stop bit 57 = 8 bit, even parity, 2 stop bits 113 = 8 bit, odd parity, 1 stop bit 121 = 8 bit, odd parity, 2 stop bits
Note on D15: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on D17: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on D19: 0 = No faults 1 = Internal Error 2 = Calibration Lost during startup 4 = Calibration memory failed 8 = Faulty/Missing Pressure sensor 1 16 = Faulty/Missing Pressure sensor 2 32 = Faulty/Missing External temperature sensor 64 = Faulty/Missing External humidity sensor 1024 = Pressure sensor 1 out of range 2048 = Pressure sensor 2 out of range 4096 = Analog input channel 1 out of range 8192 = Analog input channel 2 out of range 16384 = External temperature sensor out of range 32768 = External humidity sensor out of range
Note on D28: 0 = Always off 1 = Always on 2 = On at startup 3 = On with button press
Note on D38: 0 = 0x00 -20.4 dBm 6 = 0x06 -19.4 dBm 7 = 0x07 -18.3 dBm 8 = 0x08 -17.3 dBm 9 = 0x09 -16.4 dBm 10 = 0x0A -15.4 dBm 11 = 0x0B -14.3 dBm 12 = 0x0C -13.3 dBm 13 = 0x0D -12.3 dBm 14 = 0x0E -11.4 dBm 15 = 0x0F -10.4 dBm 16 = 0x10 -9.5 dBm 17 = 0x11 -8.4 dBm 18 = 0x12 -7.5 dBm 19 = 0x13 -6.5 dBm 20 = 0x14 -5.4 dBm 21 = 0x15 -4.5 dBm 22 = 0x16 -3.5 dBm 23 = 0x17 -2.4 dBm 24 = 0x18 -1.5 dBm 25 = 0x19 -0.3 dBm 26 = 0x1A +0.9 dBm 27 = 0x1B +2.3 dBm 28 = 0x1C +2.8 dBm 29 = 0x1D +3.9 dBm 30 = 0x1E +4.8 dBm 31 = 0x1F +5.6 dBm 32 = 0x20 +6.9 dBm 33 = 0x21 +7.5 dBm 34 = 0x22 +8.5 dBm 35 = 0x23 +10 dBm
Note on D40: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on D46: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on D53: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on D54: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V 10 = 0 = 0V, 10 = 10V 11 = 0 = 0mA, 20 = 20mA 12 = 0 = 0mA, 0.02 = 20mA
Note on D68: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on D69: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V 10 = 0 = 0V, 10 = 10V 11 = 0 = 0mA, 20 = 20mA 12 = 0 = 0mA, 0.02 = 20mA
Note on D86: 0 = Do not display any boot screen 1 = Display device type 2 = Display device type and model 3 = Display device type, model and version 4 = Display device type, model, version and addresses
Note on D91: 0 = Dual row: Show values from both channels at the same time 1 = Single row: Alternate between showing different channel values, this mode tries to make the digits as large as possible for better reading at a distance.
Note on P91: 1 = Dual row: Show values from both channels at the same time 2 = Single row: Alternate between showing different channel values, this mode tries to make the digits as large as possible for better reading at a distance.
Note on D94: 0 = Adapt font to fit on screen, use as large as possible, if it does not fit, use scrolling and smalest font 1 = 5 pixels high font 2 = 7 pixels high font 3 = 10 pixels high font
Note on P94: 1 = Adapt font to fit on screen, use as large as possible, if it does not fit, use scrolling and smalest font 2 = 5 pixels high font 3 = 7 pixels high font 4 = 10 pixels high font
Note on D95: 0 = Wrap text at the end 1 = Bounce between start and end position 2 = Wrap text at the end, sync row 1 and 2 3 = Bounce between start and end position, sync row 1 and 2
Note on P95: 1 = Wrap text at the end 2 = Bounce between start and end position 3 = Wrap text at the end, sync row 1 and 2 4 = Bounce between start and end position, sync row 1 and 2
Note on D117: 0 = Pascal [Pa] 1 = kilo Pascal [kPa] 2 = Pounds per square inch [PSI] 3 = Millibar [mBar] 4 = Inches of water column [inch H2O] 5 = Millimeters of water column [mm H2O]
Note on P117: 1 = Pascal [Pa] 2 = kilo Pascal [kPa] 3 = Pounds per square inch [PSI] 4 = Millibar [mBar] 5 = Inches of water column [inch H2O] 6 = Millimeters of water column [mm H2O]
Note on D118: 0 = Cubic meters per hour [m3/h] 1 = Cubic meters per second [m3/s] 2 = Litres per second [l/s] 3 = Cubic feet per minute [CFM]
Note on P118: 1 = Cubic meters per hour [m3/h] 2 = Cubic meters per second [m3/s] 3 = Litres per second [l/s] 4 = Cubic feet per minute [CFM]
Note on D119: 0 = Flow = Kfactor * sqrt( deltaPressure) 1 = Flow = Kfactor * sqrt( (2 * deltaPressure) / AirDensity) 2 = Flow = 1/Kfactor * sqrt( deltaPressure)
Note on P119: 1 = Flow = Kfactor * sqrt( deltaPressure) 2 = Flow = Kfactor * sqrt( (2 * deltaPressure) / AirDensity) 3 = Flow = 1/Kfactor * sqrt( deltaPressure)
Note on D122: 0 = Do not show anything 1 = Pascal [Pa] 2 = kilo Pascal [kPa] 3 = Pounds per square inch [PSI] 4 = Millibar [mBar] 5 = Inches of water column [inch H2O] 6 = Millimeters of water column [mm H2O] 7 = Cubic meters per hour [m3/h] 8 = Cubic meters per second [m3/s] 9 = Litres per second [l/s] 10 = Cubic feet per minute [CFM]
Note on P122: 1 = Do not show anything 2 = Pascal [Pa] 3 = kilo Pascal [kPa] 4 = Pounds per square inch [PSI] 5 = Millibar [mBar] 6 = Inches of water column [inch H2O] 7 = Millimeters of water column [mm H2O] 8 = Cubic meters per hour [m3/h] 9 = Cubic meters per second [m3/s] 10 = Litres per second [l/s] 11 = Cubic feet per minute [CFM]
Note on D128: 0 = Do not show anything 1 = Pascal [Pa] 2 = kilo Pascal [kPa] 3 = Pounds per square inch [PSI] 4 = Millibar [mBar] 5 = Inches of water column [inch H2O] 6 = Millimeters of water column [mm H2O] 7 = Cubic meters per hour [m3/h] 8 = Cubic meters per second [m3/s] 9 = Litres per second [l/s] 10 = Cubic feet per minute [CFM]
Note on P128: 1 = Do not show anything 2 = Pascal [Pa] 3 = kilo Pascal [kPa] 4 = Pounds per square inch [PSI] 5 = Millibar [mBar] 6 = Inches of water column [inch H2O] 7 = Millimeters of water column [mm H2O] 8 = Cubic meters per hour [m3/h] 9 = Cubic meters per second [m3/s] 10 = Litres per second [l/s] 11 = Cubic feet per minute [CFM]
Note on D139: 0 = Pascal [Pa] 1 = kilo Pascal [kPa] 2 = Pounds per square inch [PSI] 3 = Millibar [mBar] 4 = Inches of water column [inch H2O] 5 = Millimeters of water column [mm H2O]
Note on P139: 1 = Pascal [Pa] 2 = kilo Pascal [kPa] 3 = Pounds per square inch [PSI] 4 = Millibar [mBar] 5 = Inches of water column [inch H2O] 6 = Millimeters of water column [mm H2O]
Note on D140: 0 = Cubic meters per hour [m3/h] 1 = Cubic meters per second [m3/s] 2 = Litres per second [l/s] 3 = Cubic feet per minute [CFM]
Note on P140: 1 = Cubic meters per hour [m3/h] 2 = Cubic meters per second [m3/s] 3 = Litres per second [l/s] 4 = Cubic feet per minute [CFM]
Note on D141: 0 = Flow = Kfactor * sqrt( deltaPressure) 1 = Flow = Kfactor * sqrt( (2 * deltaPressure) / AirDensity) 2 = Flow = 1/Kfactor * sqrt( deltaPressure)
Note on P141: 1 = Flow = Kfactor * sqrt( deltaPressure) 2 = Flow = Kfactor * sqrt( (2 * deltaPressure) / AirDensity) 3 = Flow = 1/Kfactor * sqrt( deltaPressure)
Note on D144: 0 = Do not show anything 1 = Pascal [Pa] 2 = kilo Pascal [kPa] 3 = Pounds per square inch [PSI] 4 = Millibar [mBar] 5 = Inches of water column [inch H2O] 6 = Millimeters of water column [mm H2O] 7 = Cubic meters per hour [m3/h] 8 = Cubic meters per second [m3/s] 9 = Litres per second [l/s] 10 = Cubic feet per minute [CFM]
Note on P144: 1 = Do not show anything 2 = Pascal [Pa] 3 = kilo Pascal [kPa] 4 = Pounds per square inch [PSI] 5 = Millibar [mBar] 6 = Inches of water column [inch H2O] 7 = Millimeters of water column [mm H2O] 8 = Cubic meters per hour [m3/h] 9 = Cubic meters per second [m3/s] 10 = Litres per second [l/s] 11 = Cubic feet per minute [CFM]
Note on D150: 0 = Do not show anything 1 = Pascal [Pa] 2 = kilo Pascal [kPa] 3 = Pounds per square inch [PSI] 4 = Millibar [mBar] 5 = Inches of water column [inch H2O] 6 = Millimeters of water column [mm H2O] 7 = Cubic meters per hour [m3/h] 8 = Cubic meters per second [m3/s] 9 = Litres per second [l/s] 10 = Cubic feet per minute [CFM]
Note on P150: 1 = Do not show anything 2 = Pascal [Pa] 3 = kilo Pascal [kPa] 4 = Pounds per square inch [PSI] 5 = Millibar [mBar] 6 = Inches of water column [inch H2O] 7 = Millimeters of water column [mm H2O] 8 = Cubic meters per hour [m3/h] 9 = Cubic meters per second [m3/s] 10 = Litres per second [l/s] 11 = Cubic feet per minute [CFM]
Note on D156: 0 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 1 = Force display until remaining time is 0 2 = Show as a menu item as long as text is not empty
Note on P156: 1 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 2 = Force display until remaining time is 0 3 = Show as a menu item as long as text is not empty
Note on D208: 0 = Inactive 2 = EXOline slave 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on D209: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on D211: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s